## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-09-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.24 |  |  |  | 0.24
2 |  |  | 0.24 |  |  |  | 0.24
3 |  |  | 0.33 |  |  |  | 0.33
4 |  |  | 0.19 |  |  |  | 0.19
5 |  |  | 0.13 |  |  |  | 0.13
6 |  |  | 0.43 |  |  |  | 0.43
7 |  |  | 0.29 |  |  |  | 0.29
8 |  |  | 0.35 |  |  |  | 0.35
9 |  |  | 0.42 |  |  |  | 0.42
10 |  |  | 0.16 |  |  |  | 0.16
11 |  |  | 0.18 |  |  |  | 0.18
12 |  |  | 0.22 |  |  |  | 0.22
13 |  |  | 0.56 |  |  |  | 0.56
14 |  |  | 0.28 |  |  |  | 0.28
15 |  |  | 0.41 |  |  |  | 0.41
16 |  |  | 0.37 |  |  |  | 0.37
17 |  |  | 0.35 |  |  |  | 0.35
18 |  |  | 0.17 |  |  |  | 0.17
19 |  |  | 0.36 |  |  |  | 0.36
20 |  |  | 0.16 |  |  |  | 0.16
21 |  |  | 0.2 |  |  |  | 0.2
22 |  |  | 0.23 |  |  |  | 0.23
23 |  |  | 0.29 |  |  |  | 0.29
24 |  |  | 0.36 |  |  |  | 0.36
25 |  |  | 0.28 |  |  |  | 0.28
26 |  |  | 0.46 |  |  |  | 0.46
27 |  |  | 0.32 |  |  |  | 0.32
28 |  |  | 0.32 |  |  |  | 0.32
29 |  |  | 0.47 |  |  |  | 0.47
30 |  |  | 0.16 |  |  |  | 0.16
31
Slow Sand/Membrane/DE Filtration/Unfiltered
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: Temperature on September 1 was unavailable due to a sensor malfunction. Worst case scenario temperature of 5 degrees C was used. CT met. |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 10/00/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.76 | 149 | 113.24 | 5 | 8.2 | 80.8317 | YES | 110
2 | 0.65 | 149 | 96.85 | 15.7 | 8.15 | 38.2369 | YES | 94
3 | 0.42 | 149 | 62.58 | 17 | 8.45 | 38.1694 | YES
4 | 0.72 | 149 | 107.28 | 16.8 | 8.19 | 36.3586 | YES | 104
5 | 1.21 | 149 | 180.29 | 16.3 | 8.27 | 40.9214 | YES | 100
6 | 0.99 | 149 | 147.51 | 16.4 | 8.47 | 42.6804 | YES | 96
7 | 1.13 | 149 | 168.37 | 17.3 | 8.14 | 36.1717 | YES | 101
8 | 1.08 | 149 | 160.92 | 16.7 | 8.23 | 38.6929 | YES | 98
9 | 1.09 | 149 | 162.41 | 16 | 7.94 | 36.4636 | YES | 94
10 | 1.03 | 149 | 153.47 | 16 | 7.93 | 36.0827 | YES | 122
11 | 0.93 | 149 | 138.57 | 15.9 | 7.97 | 36.4476 | YES | 92
12 | 0.97 | 149 | 144.53 | 16.5 | 8.08 | 36.64 | YES | 81
13 | 1.08 | 149 | 160.92 | 15.8 | 7.97 | 37.3203 | YES | 105
14 | 0.82 | 149 | 122.18 | 15.8 | 7.91 | 35.4415 | YES | 106
15 | 0.6 | 149 | 89.4 | 14.8 | 7.91 | 36.9431 | YES | 94
16 | 0.52 | 149 | 77.48 | 15.9 | 7.85 | 33.2802 | YES | 96
17 | 0.69 | 149 | 102.81 | 15.8 | 7.94 | 35.3112 | YES | 89
18 | 0.67 | 149 | 99.83 | 14.5 | 7.96 | 38.6937 | YES | 97
19 | 0.9 | 149 | 134.1 | 18.1 | 7.77 | 29.1327 | YES | 99
20 | 0.73 | 149 | 108.77 | 15.5 | 7.94 | 36.1865 | YES | 94
21 | 0.59 | 149 | 87.91 | 16 | 7.78 | 32.4716 | YES | 100
22 | 0.58 | 149 | 86.42 | 14.7 | 7.84 | 36.1588 | YES | 114
23 | 0.48 | 149 | 71.52 | 14.3 | 7.79 | 36.0425 | YES | 99
24 | 0.66 | 149 | 98.34 | 15.4 | 7.85 | 34.9582 | YES | 96
25 | 0.63 | 149 | 93.87 | 14.3 | 7.88 | 37.899 | YES | 99
26 | 0.69 | 149 | 102.81 | 13.7 | 7.92 | 40.2971 | YES | 104
27 | 0.7 | 149 | 104.3 | 14.2 | 7.96 | 39.6061 | YES
28 | 0.62 | 149 | 92.38 | 16.1 | 7.29 | 26.9865 | YES
29 | 0.6 | 149 | 89.4 | 14.6 | 8 | 38.7005 | YES | 96
30 | 0.47 | 149 | 70.03 | 14 | 7.92 | 38.5305 | YES | 104
31 |  | 149
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2