## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-10-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.28 |  |  |  | 0.28
2 |  |  | 0.28 |  |  |  | 0.28
3 |  |  | 0.2 |  |  |  | 0.2
4 |  |  | 0.15 |  |  |  | 0.15
5 |  |  | 0.34 |  |  |  | 0.35
6 |  |  | 0.24 |  |  |  | 0.24
7 |  |  | 0.32 |  |  |  | 0.32
8 |  |  | 0.14 |  |  |  | 0.014
9 |  |  | 0.14 |  |  |  | 0.14
10 |  |  | 0.29 |  |  |  | 0.29
11 |  |  | 0.18 |  |  |  | 0.18
12 |  |  | 0.13 |  |  |  | 0.13
13 |  |  | 0.14 |  |  |  | 0.14
14 |  |  | 0.11 |  |  |  | 0.11
15 |  |  | 0.15 |  |  |  | 0.15
16 |  |  | 0.31 |  |  |  | 0.31
17 |  |  | 0.37 |  |  |  | 0.37
18 |  |  | 0.17 |  |  |  | 0.17
19 |  |  | 0.18 |  |  |  | 0.18
20 |  |  | 0.19 |  |  |  | 0.19
21 |  |  | 0.12 |  |  |  | 0.12
22 |  |  | 0.32 |  |  |  | 0.32
23 |  |  | 0.13 |  |  |  | 0.13
24 |  |  | 0.18 |  |  |  | 0.18
25 |  |  | off |  |  |  | off
26 |  |  | 0.38 |  |  |  | 0.38
27 |  |  | 0.19 |  |  |  | 0.19
28 |  |  | 0.21 |  |  |  | 0.21
29 |  |  | 0.14 |  |  |  | 0.14
30 |  |  | 0.19 |  |  |  | 0.19
31 |  |  | 0.15 |  |  |  | 0.15
Slow Sand/Membrane/DE Filtration/Unfiltered
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | #VALUE! |  |  | DATE: 11/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.78 | 149 | 116.22 | 14.7 | 7.87 | 37.4005 | YES | 86
2 | 0.47 | 149 | 70.03 | 13.9 | 7.85 | 37.7989 | YES | 101
3 | 0.41 | 149 | 61.09 | 13.7 | 7.83 | 37.7649 | YES | 97
4 | 0.59 | 149 | 87.91 | 14.3 | 7.82 | 36.9016 | YES | 97
5 | 0.61 | 149 | 90.89 | 13.4 | 7.82 | 39.2628 | YES | 104
6 | 0.68 | 149 | 101.32 | 13.2 | 7.84 | 40.4004 | YES | 101
7 | 0.66 | 149 | 98.34 | 14.4 | 7.91 | 38.1967 | YES | 102
8 | 0.6 | 149 | 89.4 | 13.3 | 7.88 | 40.3617 | YES | 95
9 | 1.03 | 149 | 153.47 | 13.1 | 7.87 | 42.7823 | YES | 117
10 | 1.09 | 149 | 162.41 | 14.4 | 7.9 | 39.9565 | YES | 94
11 | 1.36 | 149 | 202.64 | 13 | 7.82 | 43.8896 | YES | 103
12 | 1.17 | 149 | 174.33 | 12.5 | 7.72 | 42.7993 | YES | 107
13 | 1.15 | 149 | 171.35 | 13 | 7.74 | 41.6162 | YES
14 | 0.65 | 149 | 96.85 | 11.9 | 7.92 | 45.1796 | YES | 91
15 | 0.85 | 149 | 126.65 | 10.6 | 7.94 | 50.7553 | YES | 102
16 | 1.05 | 149 | 156.45 | 12.6 | 8 | 46.4915 | YES | 91
17 | 1.17 | 149 | 174.33 | 11.8 | 8.02 | 49.995 | YES | 101
18 | 1.41 | 149 | 210.09 | 11.5 | 7.97 | 51.5042 | YES
19 | 1.21 | 149 | 180.29 | 10.9 | 8 | 52.9666 | YES
20 | 1.17 | 149 | 174.33 | 10.1 | 8 | 55.6394 | YES
21 | 0.47 | 149 | 70.03 | 11.9 | 7.84 | 43.0421 | YES | 106
22 | 0.68 | 149 | 101.32 | 10.5 | 7.95 | 50.2897 | YES | 106
23 | 0.94 | 149 | 140.06 | 11.8 | 8.02 | 48.6982 | YES | 98
24 | 0.98 | 149 | 146.02 | 12.1 | 7.94 | 46.6137 | YES | 101
25 | 0.94 | 149 | 140.06 | 11.3 | 7.98 | 49.6391 | YES | 95
26 | 1.06 | 149 | 157.94 | 11.8 | 8.08 | 50.4359 | YES | 70
27 | 1.16 | 149 | 172.84 | 9.7 | 7.84 | 53.9067 | YES | 98
28 | 0.59 | 149 | 87.91 | 11.3 | 7.76 | 44.1312 | YES | 106
29 | 0.41 | 149 | 61.09 | 11.8 | 7.73 | 41.4093 | YES | 90
30 | 1.01 | 149 | 150.49 | 10.1 | 7.87 | 52.137 | YES | 105
31 | 0.49 | 149 | 73.01 | 10.2 | 7.87 | 48.7962 | YES | 101
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2