## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-11-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.24 |  |  | 0.24
2 |  |  |  | 0.29 |  |  | 0.29
3 |  |  |  | 0.26 |  |  | 0.26
4 |  |  |  | 0.22 |  |  | 0.22
5 |  |  |  | 0.42 |  |  | 0.42
6 |  |  |  | 0.24 |  |  | 0.24
7 |  |  |  | 0.16 |  |  | 0.16
8 |  |  |  | 0.21 |  |  | 0.21
9 |  |  |  | 0.24 |  |  | 0.24
10 |  |  |  | 0.31 |  |  | 0.31
11 |  |  |  | 0.03 |  |  | 0.03
12 |  |  |  | 0.17 |  |  | 0.17
13 |  |  |  | 0.16 |  |  | 0.16
14 |  |  |  | 0.2 |  |  | 0.2
15 |  |  |  | 0.21 |  |  | 0.21
16 |  |  |  | 0.25 |  |  | 0.25
17 |  |  |  | 0.27 |  |  | 0.27
18 |  |  |  | 0.21 |  |  | 0.21
19 |  |  |  | 0.24 |  |  | 0.24
20 |  |  |  | 0.21 |  |  | 0.21
21 |  |  |  | 0.17 |  |  | 0.17
22 |  |  |  | 0.21 |  |  | 0.21
23 |  |  |  | 0.11 |  |  | 0.11
24 |  |  |  | 0.22 |  |  | 0.22
25 |  |  |  | 0.19 |  |  | 0.19
26 |  |  |  | 0.23 |  |  | 0.23
27 |  |  |  | 0.32 |  |  | 0.32
28 |  |  |  | 0.19 |  |  | 0.19
29 |  |  |  | 0.52 |  |  | 0.52
30 |  |  |  | 0.21 |  |  | 0.21
31
Slow Sand/Membrane/DE Filtration/Unfiltered
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 12/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-11-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.43 | 149 | 64.07 | 11.7 | 7.75 | 42.0685 | YES | 107
2 | 0.91 | 149 | 135.59 | 12.2 | 7.79 | 43.5754 | YES | 87
3 | 0.9 | 149 | 134.1 | 12.9 | 7.65 | 39.3961 | YES | 97
4 | 0.81 | 149 | 120.69 | 12.6 | 7.65 | 39.7803 | YES | 100
5 | 0.41 | 149 | 61.09 | 11.4 | 7.76 | 42.9599 | YES | 101
6 | 0.44 | 149 | 65.56 | 11.3 | 7.85 | 44.7852 | YES | 100
7 | 0.69 | 149 | 102.81 | 10.8 | 7.77 | 46.2979 | YES | 107
8 | 0.65 | 149 | 96.85 | 10.3 | 7.69 | 46.3139 | YES
9 | 0.68 | 149 | 101.32 | 11 | 7.81 | 46.2857 | YES
10 | 0.69 | 149 | 102.81 | 10.7 | 7.78 | 46.7712 | YES
11 | 1.62 | 149 | 241.38 | 10.1 | 7.74 | 53.383 | YES | 99
12 | 1.14 | 149 | 169.86 | 11.3 | 7.75 | 46.8044 | YES | 102
13 | 1.8 | 149 | 268.2 | 11.4 | 7.74 | 49.9507 | YES | 97
14 | 1.04 | 149 | 154.96 | 12.4 | 7.97 | 46.4982 | YES | 100
15 | 1.02 | 149 | 151.98 | 11.9 | 7.99 | 48.3012 | YES
16 | 1.07 | 149 | 159.43 | 13.6 | 7.44 | 35.4807 | YES | 96
17 | 1.04 | 149 | 154.96 | 11.9 | 7.67 | 43.2413 | YES
18 | 1.02 | 149 | 151.98 | 10.7 | 7.63 | 46.0501 | YES
19 | 1.04 | 149 | 154.96 | 10 | 7.66 | 48.8702 | YES
20 | 1.01 | 149 | 150.49 | 9.7 | 7.77 | 51.6747 | YES
21 | 0.96 | 149 | 143.04 | 12.9 | 7.39 | 36.0381 | YES | off
22 | 1.43 | 149 | 213.07 | 11.5 | 7.68 | 46.5676 | YES | 98
23 | 1.28 | 149 | 190.72 | 10.2 | 8.05 | 56.9881 | YES | 112
24 | 1.14 | 149 | 169.86 | 10.1 | 8.15 | 58.5239 | YES
25 | 1.04 | 149 | 154.96 | 8.9 | 8.07 | 60.9647 | YES
26 | 1.02 | 149 | 151.98 | 8.7 | 8.04 | 60.9891 | YES
27 | 1.01 | 149 | 150.49 | 9.1 | 7.98 | 58.0171 | YES
28 | 1.28 | 149 | 190.72 | 10.6 | 8.81 | 73.0931 | YES | 86
29 | 0.93 | 149 | 138.57 | 10.5 | 8.43 | 61.5056 | YES | 67
30 | 0.91 | 149 | 135.59 | 10.5 | 8.49 | 62.7116 | YES | 89
31 |  | 149
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2