## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-01-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.34 |  |  | 0.34 | 0.34
2 |  |  |  | 0.36 |  |  | 0.36 | 0.36
3 |  |  |  | 0.26 |  |  | 0.26 | 0.26
4 |  |  |  | 0.11 |  |  | 0.11 | 0.11
5 |  |  |  | 0.44 |  |  | 0.44 | 0.44
6 |  |  |  | 0.44 |  |  | 0.44 | 0.44
7 |  |  |  | 0.22 |  |  | 0.22 | 0.22
8 |  |  |  | 0.18 |  |  | 0.18 | 0.18
9 |  |  |  | 0.27 |  |  | 0.27 | 0.27
10 |  |  |  | 0.23 |  |  | 0.23 | 0.23
11 |  |  |  | 0.21 |  |  | 0.21 | 0.21
12 |  |  |  | 0.22 |  |  | 0.22 | 0.22
13 |  |  |  | 0.19 |  |  | 0.19 | 0.19
14 |  |  |  | 0.18 |  |  | 0.18 | 0.18
15 |  |  |  | 0.17 |  |  | 0.17 | 0.17
16 |  |  |  | 0.14 |  |  | 0.14 | 0.14
17 |  |  |  | 0.27 |  |  | 0.27 | 0.27
18 |  |  |  | 0.22 |  |  | 0.22 | 0.22
19 |  |  |  | 0.21 |  |  | 0.21 | 0.21
20 |  |  |  | 0.21 |  |  | 0.21 | 0.21
21 |  |  |  | 0.23 |  |  | 0.23 | 0.23
22 |  |  |  | 0.22 |  |  | 0.22 | 0.22
23 |  |  |  | 0.15 |  |  | 0.15 | 0.15
24 |  |  |  | 0.16 |  |  | 0.16 | 0.16
25 |  |  |  | 0.13 |  |  | 0.13 | 0.13
26 |  |  |  | 0.34 |  |  | 0.34 | 0.34
27 |  |  |  | 0.3 |  |  | 0.3 | 0.3
28 |  |  |  | 0.32 |  |  | 0.32 | 0.32
29 |  |  |  | 0.19 |  |  | 0.19 | 0.19
30 |  |  |  | 0.09 |  |  | 0.09 | 0.09
31 |  |  |  | 0.13 |  |  | 0.13 | 0.13
Slow Sand/Membrane/DE Filtration/Unfiltered
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 2/10/2026
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2026-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.58 | 149 | 235.42 | 7.8 | 7.71 | 61.4066 | YES | 104
2 | 1.8 | 149 | 268.2 | 9.3 | 7.65 | 55.6908 | YES | 94
3 | 1.75 | 149 | 260.75 | 9.2 | 7.75 | 57.788 | YES | 84
4 | 1.64 | 149 | 244.36 | 8.6 | 7.79 | 60.2869 | YES | 106
5 | 1.53 | 149 | 227.97 | 9.4 | 7.75 | 55.5803 | YES | 105
6 | 1.05 | 149 | 156.45 | 10.2 | 7.92 | 52.9656 | YES | 100
7 | 1.24 | 149 | 184.76 | 7.8 | 8.03 | 66.2907 | YES | 91
8 | 1.19 | 149 | 177.31 | 9.5 | 7.87 | 55.4204 | YES | 104
9 | 0.98 | 149 | 146.02 | 7.5 | 7.85 | 61.4844 | YES | 121
10 | 0.97 | 149 | 144.53 | 7.1 | 7.86 | 63.3365 | YES
11 | 0.99 | 149 | 147.51 | 7.3 | 7.87 | 62.8532 | YES
12 | 1.11 | 149 | 165.39 | 9.5 | 8.3 | 64.1373 | YES | 94
13 | 1.09 | 149 | 162.41 | 8.7 | 8.26 | 66.603 | YES | 92
14 | 1.49 | 149 | 222.01 | 8.5 | 8.18 | 68.7264 | YES | 104
15 | 1.34 | 149 | 199.66 | 8.2 | 8.12 | 67.4374 | YES | 97
16 | 1.56 | 149 | 232.44 | 8.3 | 8.04 | 66.751 | YES | 108
17 | 1.59 | 149 | 236.91 | 9.2 | 8.11 | 64.6178 | YES | 94
18 | 1.37 | 149 | 204.13 | 7.7 | 8.11 | 69.7776 | YES | 89
19 | 1.3 | 149 | 193.7 | 8.2 | 8.1 | 66.6348 | YES | 97
20 | 1.11 | 149 | 165.39 | 7.7 | 8.15 | 68.6767 | YES | 100
21 | 1.65 | 149 | 245.85 | 6.8 | 8.07 | 75.6021 | YES | 96
22 | 1.45 | 149 | 216.05 | 7.1 | 8.01 | 70.7615 | YES | 83
23 | 1.67 | 149 | 248.83 | 6.6 | 8.02 | 75.4346 | YES | 93
24 | 1.8 | 149 | 268.2 | 7.6 | 7.85 | 67.2021 | YES | 96
25 | 1.51 | 149 | 224.99 | 8.1 | 7.69 | 59.2513 | YES | 101
26 | 1.47 | 149 | 219.03 | 6.9 | 8.01 | 71.9088 | YES | 90
27 | 1.52 | 149 | 226.48 | 5.7 | 7.82 | 73.2717 | YES | 96
28 | 1.31 | 149 | 195.19 | 7.4 | 7.79 | 62.9459 | YES | 106
29 | 1.84 | 149 | 274.16 | 7.8 | 7.91 | 68.0732 | YES | 95
30 | 1.85 | 149 | 275.65 | 8.1 | 8 | 68.9965 | YES | 91
31 | 1.83 | 149 | 272.67 | 9.3 | 8.1 | 65.7643 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2