## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-02-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.09 |  |  | 0.09
2 |  |  |  | 0.31 |  |  | 0.31
3 |  |  |  | 0.3 |  |  | 0.3
4 |  |  |  | 0.29 |  |  | 0.29
5 |  |  |  | 0.22 |  |  | 0.22
6 |  |  |  | 0.25 |  |  | 0.25
7 |  |  |  | 0.48 |  |  | 0.48
8 |  |  |  | 0.33 |  |  | 0.33
9 |  |  |  | 0.19 |  |  | 0.19
10 |  |  |  | 0.27 |  |  | 0.27
11 |  |  |  | 0.49 |  |  | 0.49
12 |  |  |  | 0.28 |  |  | 0.28
13 |  |  |  | 0.21 |  |  | 0.21
14 |  |  |  | 0.19 |  |  | 0.19
15 |  |  |  | 0.23 |  |  | 0.23
16 |  |  |  | 0.23 |  |  | 0.23
17 |  |  |  | 0.22 |  |  | 0.22
18 |  |  |  | 0.31 |  |  | 0.31
19 |  |  |  | 0.15 |  |  | 0.15
20 |  |  |  | 0.47 |  |  | 0.47
21 |  |  |  | 0.11 |  |  | 0.11
22 |  |  |  | 0.24 |  |  | 0.24
23 |  |  |  | 0.15 |  |  | 0.15
24 |  |  |  | 0.27 |  |  | 0.27
25 |  |  |  | 0.2 |  |  | 0.2
26 |  |  |  | 0.14 |  |  | 0.14
27 |  |  |  | 0.38 |  |  | 0.38
28 |  |  |  | 0.29 |  |  | 0.29
29
30
31
Slow Sand/Membrane/DE Filtration/Unfiltered
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 3/11/2026
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2026-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.82 | 149 | 271.18 | 9.4 | 8.3 | 70.176 | YES
2 | 1.79 | 149 | 266.71 | 9.7 | 8.09 | 63.4648 | YES | 88
3 | 1.51 | 149 | 224.99 | 8.7 | 8.06 | 65.045 | YES | 97
4 | 1.12 | 149 | 166.88 | 9.3 | 8.03 | 59.0268 | YES | 89
5 | 1.11 | 149 | 165.39 | 9.7 | 8.07 | 58.217 | YES
6 | 1.15 | 149 | 171.35 | 9.7 | 7.8 | 53.0788 | YES | 84
7 | 1.24 | 149 | 184.76 | 9.6 | 7.8 | 53.9932 | YES | 95
8 | 1.39 | 149 | 207.11 | 9.1 | 7.81 | 57.0245 | YES | 98
9 | 1.35 | 149 | 201.15 | 8.7 | 7.7 | 56.0522 | YES | 81
10 | 1.71 | 149 | 254.79 | 7.3 | 7.78 | 66.1668 | YES | 107
11 | 1.63 | 149 | 242.87 | 7.5 | 7.72 | 63.2679 | YES | 82
12 | 1.21 | 149 | 180.29 | 8.5 | 7.81 | 58.1609 | YES | 85
13 | 1.48 | 149 | 220.52 | 8 | 7.87 | 63.4512 | YES | 93
14 | 1.47 | 149 | 219.03 | 8.3 | 7.83 | 61.2029 | YES
15 | 1.39 | 149 | 207.11 | 8.6 | 7.78 | 58.3516 | YES
16 | 1.27 | 149 | 189.23 | 8.2 | 7.83 | 60.2035 | YES
17 | 1.27 | 149 | 189.23 | 8.1 | 7.69 | 57.6254 | YES
18 | 1.44 | 149 | 214.56 | 7.5 | 8.09 | 70.806 | YES | 96
19 | 1.83 | 149 | 272.67 | 5.7 | 8.1 | 84.257 | YES | 93
20 | 1.34 | 149 | 199.66 | 5.6 | 8.12 | 80.6465 | YES | 90
21 | 1.58 | 149 | 235.42 | 8.4 | 7.3 | 50.89 | YES | 98
22 | 1.46 | 149 | 217.54 | 8.1 | 7.39 | 52.8867 | YES | 101
23 | 1.65 | 149 | 245.85 | 8.6 | 7.61 | 56.562 | YES | 89
24 | 1.23 | 149 | 183.27 | 6.9 | 7.71 | 62.6753 | YES | 89
25 | 1.48 | 149 | 220.52 | 6.9 | 7.75 | 65.4758 | YES | 112
26 | 1.6 | 149 | 238.4 | 6.9 | 8.04 | 73.8248 | YES | 93
27 | 1.38 | 149 | 205.62 | 7.2 | 7.66 | 61.3695 | YES | 89
28 | 1.48 | 149 | 220.52 | 7.5 | 7.83 | 64.7042 | YES | 90
29 |  | 149
30 |  | 149
31 |  | 149
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2