## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-03-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.29 |  |  | 0.29 | 0.29
2 |  |  |  | 0.37 |  |  | 0.37 | 0.37
3 |  |  |  | 0.22 |  |  | 0.22 | 0.22
4 |  |  |  | 0.3 |  |  | 0.3 | 0.3
5 |  |  |  | 0.19 |  |  | 0.19 | 0.19
6 |  |  |  | 0.37 |  |  | 0.37 | 0.37
7 |  |  |  | 0.15 |  |  | 0.15 | 0.15
8 |  |  |  | 0.28 |  |  | 0.28 | 0.28
9 |  |  |  | 0.37 |  |  | 0.37 | 0.37
10 |  |  |  | 0.24 |  |  | 0.24 | 0.24
11 |  |  |  | 0.16 |  |  | 0.16 | 0.16
12 |  |  |  | 0.26 |  |  | 0.26 | 0.26
13 |  |  |  | 0.45 |  |  | 0.45 | 0.45
14 |  |  |  | 0.33 |  |  | 0.33 | 0.33
15 |  |  |  | 0.61 |  |  | 0.61 | 0.61
16 |  |  |  | 0.27 |  |  | 0.27 | 0.27
17 |  |  |  | 0.17 |  |  | 0.17 | 0.17
18 |  |  |  | 0.18 |  |  | 0.18 | 0.18
19 |  |  |  | 0.25 |  |  | 0.25 | 0.25
20 |  |  |  | 0.66 |  |  | 0.66 | 0.66
21 |  |  |  | 0.34 |  |  | 0.34 | 0.34
22 |  |  |  | 0.31 |  |  | 0.31 | 0.31
23 |  |  |  | 0.28 |  |  | 0.28 | 0.28
24 |  |  |  | 0.48 |  |  | 0.48 | 0.48
25 |  |  |  | 0.47 |  |  | 0.47 | 0.47
26 |  |  |  | 0.16 |  |  | 0.16 | 0.16
27 |  |  |  | 0.22 |  |  | 0.22 | 0.22
28 |  |  |  | 0.19 |  |  | 0.19 | 0.19
29 |  |  |  | 0.21 |  |  | 0.21 | 0.21
30 |  |  |  | 0.25 |  |  | 0.25 | 0.25
31 |  |  |  | 0.24 |  |  | 0.24 | 0.24
Slow Sand/Membrane/DE Filtration/Unfiltered
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | Yes |  | Yes
Notes: Contact Time on 3/15/2026 based on actual PHF rather than assumed PHF. |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 4/10/2026
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2026-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.51 | 149 | 224.99 | 7.5 | 7.64 | 60.6073 | YES | 105
2 | 1.09 | 149 | 162.41 | 7.8 | 7.73 | 58.4301 | YES | 105
3 | 1.2 | 149 | 178.8 | 8.4 | 7.72 | 56.6217 | YES | 95
4 | 1.13 | 149 | 168.37 | 8.7 | 7.69 | 54.4511 | YES | 91
5 | 1.46 | 149 | 217.54 | 8.1 | 7.84 | 62.1935 | YES | 97
6 | 1.62 | 149 | 241.38 | 8.4 | 7.91 | 63.6802 | YES | 91
7 | 1.33 | 149 | 198.17 | 9.6 | 7.99 | 58.416 | YES | 100
8 | 1.14 | 149 | 169.86 | 9.4 | 7.7 | 52.1955 | YES | 98
9 | 0.94 | 149 | 140.06 | 8.8 | 7.75 | 54.0654 | YES | 95
10 | 1.1 | 149 | 163.9 | 8 | 7.8 | 59.1875 | YES | 91
11 | 0.96 | 149 | 143.04 | 7.9 | 7.94 | 61.6742 | YES | 96
12 | 0.84 | 149 | 125.16 | 8.1 | 8.01 | 61.5382 | YES | 87
13 | 0.47 | 149 | 70.03 | 8.6 | 8.27 | 62.6017 | YES | 94
14 | 0.66 | 149 | 98.34 | 7.7 | 7.97 | 61.0328 | YES | 119
15 | 0.41 | 302 | 123.82 | 8.5 | 8.24 | 61.9131 | YES | 103
16 | 0.46 | 149 | 68.54 | 8.3 | 8.19 | 61.9939 | YES | 102
17 | 0.54 | 149 | 80.46 | 9.3 | 8.41 | 63.3128 | YES | 87
18 | 1.08 | 149 | 160.92 | 9.1 | 8.28 | 65.2051 | YES | 89
19 | 1.41 | 149 | 210.09 | 9.2 | 8.27 | 67.0656 | YES | 84
20 | 1.66 | 149 | 247.34 | 9.7 | 8.14 | 63.6547 | YES | 87
21 | 1.45 | 149 | 216.05 | 9.8 | 7.81 | 54.7724 | YES | 98
22 | 1.59 | 149 | 236.91 | 9.1 | 7.74 | 56.9069 | YES | 99
23 | 1.48 | 149 | 220.52 | 9.1 | 7.85 | 58.4588 | YES | 88
24 | 1.41 | 149 | 210.09 | 9.2 | 7.84 | 57.3884 | YES | 87
25 | 1.44 | 149 | 214.56 | 8.8 | 7.93 | 61.126 | YES | 87
26 | 1.33 | 149 | 198.17 | 8.3 | 7.78 | 59.1364 | YES | 85
27 | 1.39 | 149 | 207.11 | 8.3 | 7.89 | 61.9679 | YES | 95
28 | 1.52 | 149 | 226.48 | 9.6 | 7.41 | 48.5123 | YES | 100
29 | 1.45 | 149 | 216.05 | 9 | 7.49 | 51.5411 | YES | 110
30 | 1.4 | 149 | 208.6 | 8.5 | 7.53 | 53.7584 | YES | 91
31 | 1.64 | 149 | 244.36 | 8.7 | 7.65 | 56.9301 | YES | 83
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2