## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-12-24
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.038 |  | 0.04 | 0.036 | 0.04
2 | 0.043 |  |  | 0.048 | 0.034 |  | 0.05
3 |  |  | 0.066 | 0.046 |  |  | 0.05
4 |  |  |  | 0.032 | 0.036 | 0.035 | 0.04
5 | 0.036 |  |  | 0.028 |  |  | 0.04
6 | 0.025 | 0.03 | 0.031 | 0.03 |  |  | 0.03
7 | 0.033 | 0.031 |  |  |  |  | 0.03
8 |  |  |  | 0.147 | 0.077 | 0.094 | 0.15
9 | 0.038 | 0.05 |  | 0.059 |  |  | 0.06
10 | 0.04 |  |  | 0.03 | 0.027 | 0.033 | 0.04
11 |  |  |  | 0.035 | 0.028 | 0.0259 | 0.04
12 |  |  |  | 0.0417 | 0.048 | 0.04 | 0.05
13 | 0.036 |  |  | 0.047 | 0.048 | 0.055 | 0.06
14 | off | off | off | off | off | off | off
15 |  |  |  | 0.049 | 0.039 | 0.033 | 0.05
16 |  |  |  | 0.055 | 0.052 | 0.042 | 0.06
17 | off | off | off | off | off | off | off
18 |  |  |  | 0.053 | 0.077 | 0.094 | 0.09
19 | 0.055 | 0.056 | 0.05 | 0.045 |  |  | 0.06
20 |  | 0.049 |  |  |  |  | 0.05
21 |  | 0.044 |  | 0.0374 | 0.036 |  | 0.04
22 |  |  | 0.046 | 0.034 | 0.036 |  | 0.05
23 |  |  |  | 0.036 | 0.03 | 0.033 | 0.04
24 |  |  |  | 0.061 | 0.058 | 0.056 | 0.06
25 |  |  |  |  | 0.085 | 0.057 | 0.09
26 | 0.055 | 0.051 |  |  | 0.085 | 0.057 | 0.09
27 | [6 empty] | printer malfunction
28 | 0.045 | 0.051 |  |  | 0.041 | 0.057 | 0.06
29 |  |  |  | 0.068 | 0.057 | 0.061 | 0.07
30 | off | off | off | off | off | off | off
31 | [5 empty] | 0.227 | 0.23
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Eric Bufkin
[5 empty] | SIGNATURE: |  |  | DATE: 01/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-12-24 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.11 | 241 | 267.51 | 7.2 | 8.74 | 88.3143 | YES | 192
2 | 1.12 | 241 | 269.92 | 6.1 | 8.78 | 96.8885 | YES | 192
3 | 1.02 | 241 | 245.82 | 6.5 | 8.74 | 91.7323 | YES | 188
4 | 1.06 | 241 | 255.46 | 6 | 8.73 | 95.0857 | YES | 174
5 | 0.99 | 241 | 238.59 | 6.2 | 8.73 | 92.9889 | YES | 200
6 | 0.94 | 241 | 226.54 | 6.9 | 8.33 | 75.9662 | YES | 193
7 | 0.98 | 241 | 236.18 | 8 | 8.55 | 76.7074 | YES | 163
8 | 0.89 | 241 | 214.49 | 8.4 | 8.57 | 74.3781 | YES | 161
9 | 1.09 | 241 | 262.69 | 7.1 | 8.69 | 87.0915 | YES | 181
10 | 1.01 | 241 | 243.41 | 7.2 | 8.69 | 85.6705 | YES | 196
11 | 0.99 | 241 | 238.59 | 6.9 | 8.47 | 80.4557 | YES | 177
12 | 1.03 | 241 | 248.23 | 7.2 | 8.54 | 81.2472 | YES | 175
13 | 1.08 | 241 | 260.28 | 7.3 | 8.43 | 77.944 | YES | 204
14 | 0.97 | 241 | 233.77 | 7 | 7.93 | 65.4128 | YES | 166
15 | 1.07 | 241 | 257.87 | 8 | 8.33 | 71.5161 | YES
16 | 1.05 | 241 | 253.05 | 7.1 | 8.12 | 70.2835 | YES | 186
17 | 1.04 | 241 | 250.64 | 9.6 | 8.03 | 57.3066 | YES | 181
18 | 1.64 | 241 | 395.24 | 7.8 | 7.96 | 67.7199 | YES | off
19 | 1.24 | 241 | 298.84 | 10.3 | 8.01 | 55.5387 | YES | 189
20 | 1.15 | 241 | 277.15 | 8.8 | 7.75 | 55.3907 | YES | 179
21 | 1.07 | 241 | 257.87 | 9.1 | 8.18 | 62.8058 | YES | 177
22 | 0.99 | 241 | 238.59 | 8.9 | 8.21 | 63.7665 | YES | 162
23 | 1.27 | 241 | 306.07 | 8.8 | 8.02 | 61.9142 | YES | 167
24 | 1.09 | 241 | 262.69 | 8.9 | 8.09 | 61.7662 | YES | 177
25 | 1.01 | 241 | 243.41 | 8.2 | 8.54 | 75.647 | YES | 172
26 | 1.11 | 241 | 267.51 | 9 | 8.47 | 70.6113 | YES | 174
27 | 1.11 | 241 | 267.51 | 8.6 | 8.5 | 73.3801 | YES | 162
28 | 1.31 | 241 | 315.71 | 9 | 8.37 | 69.6951 | YES
29 | 1.11 | 241 | 267.51 | 9 | 8.49 | 71.1297 | YES | 197
30 | 1.34 | 241 | 322.94 | 8.4 | 8.45 | 75.0525 | YES | 171
31 | 1.29 | 241 | 310.89 | 7.9 | 8.49 | 78.372 | YES | 159
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2