## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-01-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.069 | 0.073 | 0.148 |  |  |  | 0.15
2 |  |  |  | 0.091 | 0.035 | 0.048 | 0.09
3 | 0.055 | 0.077 |  |  | 0.037 | 0.046 | 0.08
4 |  |  |  | 0.072 | 0.039 | 0.044 | 0.07
5 |  |  |  | 0.044 |  | 0.042 | 0.04
6 |  |  |  | 0.05 | 0.051 | 0.051 | 0.05
7 |  |  |  | 0.118 | 0.073 | 0.076 | 0.12
8 |  |  |  | 0.111 | 0.07 |  | 0.11
9 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 |  |  |  |  | 0.048 | 0.044 | 0.05
11 | 0.043 | 0.037 | 0.039 | 0.044 |  |  | 0.04
12 |  | 0.075 | 0.032 |  | 0.035 | 0.037 | 0.08
13 |  |  |  | 0.035 | 0.038 | 0.035 | 0.04
14 |  |  |  | 0.049 | 0.045 | 0.038 | 0.05
15 |  |  |  | 0.03 | 0.032 | 0.035 | 0.04
16 |  |  |  | 0.03 |  |  | 0.03
17 |  |  |  | 0.037 | 0.065 | 0.047 | 0.07
18 |  |  |  | 0.038 | 0.06 | 0.041 | 0.06
19 |  |  |  |  | 0.042 | 0.043 | 0.04
20 |  |  |  |  | 0.04 | 0.038 | 0.04
21 |  |  |  | 0.035 | 0.046 | 0.036 | 0.05
22 |  |  |  | 0.045 | 0.034 | 0.036 | 0.05
23 |  |  |  | 0.041 | 0.037 | 0.036 | 0.04
24 |  |  |  | 0.042 | 0.038 | 0.037 | 0.04
25 |  |  |  | 0.037 | 0.065 | 0.039 | 0.07
26 |  |  |  | 0.038 | 0.039 | 0.043 | 0.04
27 |  |  |  | 0.049 | 0.053 | 0.04 | 0.05
28 |  |  |  | 0.046 | 0.037 | 0.054 | 0.05
29 |  |  |  | 0.062 | 0.043 |  | 0.06
30 |  |  |  | 0.038 | 0.04 | 0.04 | 0.04
31 |  |  |  | 0.032 | 0.089 |  | 0.09
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 02/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-01-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.16 | 241 | 279.56 | 7.8 | 8.49 | 77.7115 | YES | 167
2 | 1.24 | 241 | 298.84 | 8.1 | 8.39 | 74.0722 | YES | 162
3 | 1.21 | 241 | 291.61 | 8.1 | 8.43 | 74.9019 | YES | 180
4 | 1.28 | 241 | 308.48 | 8 | 7.48 | 53.86 | YES | 169
5 | 1.5 | 241 | 361.5 | 8.7 | 7.66 | 56.2178 | YES | 167
6 | 1.21 | 241 | 291.61 | 8.1 | 8.19 | 68.6033 | YES | 194
7 | 1.16 | 241 | 279.56 | 8.1 | 7.66 | 56.2854 | YES | 185
8 | 1.25 | 241 | 301.25 | 7.9 | 8.06 | 66.6405 | YES | 174
9 | 1.3 | 241 | 313.3 | 8.1 | 8.02 | 65.1661 | YES | 175
10 | 1.21 | 241 | 291.61 | 8 | 8.11 | 67.0882 | YES | 167
11 | 1.03 | 241 | 248.23 | 7.7 | 7.44 | 52.6392 | YES | 168
12 | 1.1 | 241 | 265.1 | 8.1 | 7.6 | 54.7048 | YES | 172
13 | 1.12 | 241 | 269.92 | 7.6 | 8.03 | 66.2659 | YES | 180
14 | 1.25 | 241 | 301.25 | 7.1 | 7.98 | 68.3662 | YES | 175
15 | 1.15 | 241 | 277.15 | 6.7 | 7.93 | 68.1901 | YES | 183
16 | 1.3 | 241 | 313.3 | 6.8 | 7.83 | 66.4585 | YES | 174
17 | 1.11 | 241 | 267.51 | 6.6 | 7.83 | 65.8918 | YES
18 | 1.84 | 241 | 443.44 | 6.6 | 7.33 | 59.8437 | YES | 181
19 | 1.48 | 241 | 356.68 | 6.5 | 7.37 | 58.6261 | YES | 170
20 | 1.05 | 241 | 253.05 | 5.8 | 7.67 | 65.1966 | YES | 171
21 | 1.07 | 241 | 257.87 | 5.7 | 7.94 | 72.6142 | YES | 183
22 | 1.43 | 241 | 344.63 | 5 | 7.89 | 78.0613 | YES | 190
23 | 1.23 | 241 | 296.43 | 5.3 | 8.1 | 80.6748 | YES | 189
24 | 1.3 | 241 | 313.3 | 5.5 | 8.05 | 78.7652 | YES | 184
25 | 1.06 | 241 | 255.46 | 5.5 | 7.82 | 70.3728 | YES | 170
26 | 1.12 | 241 | 269.92 | 5.8 | 7.91 | 71.7499 | YES | 177
27 | 1.27 | 241 | 306.07 | 4.7 | 7.94 | 79.6544 | YES | 193
28 | 1.29 | 241 | 310.89 | 4.6 | 7.67 | 72.8038 | YES | 188
29 | 1.24 | 241 | 298.84 | 4.9 | 7.72 | 72.2099 | YES | 193
30 | 1.2 | 241 | 289.2 | 5.5 | 7.71 | 68.7212 | YES | 180
31 | 1.27 | 241 | 306.07 | 6.9 | 7.6 | 60.5082 | YES | 175
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2