## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-03-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | [5 empty] | 0.117 | 0.12
2 | 0.143 | 0.164 |  | 0.09 | 0.055 | 0.069 | 0.16
3 | 0.101 |  |  | 0.055 | 0.032 |  | 0.1
4 |  |  | 0.034 | 0.036 | 0.037 |  | 0.041
5 |  |  | 0.04 |  | 0.026 |  | 0.04
6 |  |  | 0.037 | 0.041 | 0.041 |  | 0.04
7 |  |  |  | 0.039 | 0.039 | 0.034 | 0.04
8 |  |  |  | 0.04 | 0.039 | 0.045 | 0.05
9 |  |  |  | 0.069 | 0.032 | 0.044 | 0.07
10 |  |  | 0.079 | 0.038 |  |  | 0.08
11 |  |  | 0.036 | 0.045 |  |  | 0.05
12 |  |  | 0.039 | 0.044 | 0.044 |  | 0.04
13 |  |  | 0.043 | 0.039 | 0.043 |  | 0.04
14 |  |  | 0.031 | 0.038 | 0.036 |  | 0.04
15 |  |  | 0.08 | 0.194 | 0.052 |  | 0.19
16 |  |  |  | 0.076 | 0.04 | 0.044 | 0.08
17 |  |  |  | 0.086 | 0.06 |  | 0.09
18 |  |  |  | 0.08 | 0.06 | 0.053 | 0.08
19 | 0.215 |  |  | 0.29 | 0.101 | 0.045 | 0.29
20 |  |  |  |  | 0.32 | 0.034 | 0.32
21 |  |  |  | 0.045 | 0.049 | 0.095 | 0.1
22 |  |  |  |  | 0.028 | 0.044 | 0.04
23 | 0.041 |  |  | 0.023 | 0.025 |  | 0.04
24 |  |  |  | 0.024 | 0.024 | 0.025 | 0.03
25 |  |  |  | 0.037 | 0.024 | 0.04 | 0.04
26 |  |  |  | 0.034 | 0.027 | 0.025 | 0.03
27 |  |  |  | 0.033 | 0.063 |  | 0.06
28 | off | off | off | off | off | off | off
29 | off | off | off | off | off | off | off
30 |  |  |  | 0.086 |  |  | 0.09
31 |  |  |  | 0.218 | 0.078 | 0.081 | 0.22
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | YES |  | YES
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 04/10/25
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.14 | 241 | 274.74 | 8.6 | 8.37 | 70.2175 | YES | 167
2 | 0.96 | 241 | 231.36 | 8.7 | 8.09 | 61.6713 | YES | 150
3 | 1.1 | 241 | 265.1 | 10.7 | 8.26 | 58.1986 | YES | 192
4 | 1.12 | 241 | 269.92 | 8.6 | 8.8 | 82.0359 | YES | 181
5 | 1.39 | 241 | 334.99 | 8 | 8.49 | 78.7585 | YES | 185
6 | 1.08 | 241 | 260.28 | 8.1 | 8.47 | 74.8531 | YES | 186
7 | 1.14 | 241 | 274.74 | 8.3 | 8.61 | 78.2779 | YES | 180
8 | 1.02 | 241 | 245.82 | 8.1 | 7.83 | 58.879 | YES | 174
9 | 0.94 | 241 | 226.54 | 8.7 | 8.12 | 62.2004 | YES | 172
10 | 1.15 | 241 | 277.15 | 9 | 8.2 | 64.2932 | YES | 179
11 | 1.13 | 241 | 272.33 | 8.3 | 8.14 | 65.8296 | YES | 176
12 | 1.05 | 241 | 253.05 | 8.3 | 7.95 | 60.8723 | YES | 173
13 | 1.16 | 241 | 279.56 | 7.8 | 7.91 | 62.8714 | YES | 171
14 | 1.3 | 241 | 313.3 | 7 | 7.94 | 68.2375 | YES | 191
15 | 1.14 | 241 | 274.74 | 7.5 | 7.85 | 62.6409 | YES | 169
16 | 1.02 | 241 | 245.82 | 7.3 | 7.58 | 56.7969 | YES | 160
17 | 1.02 | 241 | 245.82 | 8.2 | 7.62 | 54.2266 | YES | 191
18 | 1.26 | 241 | 303.66 | 7.3 | 7.64 | 59.6765 | YES | 193
19 | 1.08 | 241 | 260.28 | 7.9 | 7.51 | 53.5617 | YES | 176
20 | 1.1 | 241 | 265.1 | 7.74 | 7.69 | 57.8946 | YES | 175
21 | 1.13 | 241 | 272.33 | 8.7 | 8.01 | 61.1073 | YES | 176
22 | 1.05 | 241 | 253.05 | 8.5 | 7.46 | 50.3653 | YES | 170
23 | 1.03 | 241 | 248.23 | 9 | 7.5 | 49.2967 | YES | 174
24 | 0.95 | 241 | 228.95 | 9.3 | 7.4 | 46.2168 | YES | 173
25 | 1.05 | 241 | 253.05 | 11.5 | 8.14 | 52.5136 | YES | 156
26 | 1.06 | 241 | 255.46 | 10.1 | 7.55 | 46.7959 | YES | 169
27 | 1.08 | 241 | 260.28 | 10.5 | 7.53 | 45.3535 | YES | 177
28 | 0.94 | 241 | 226.54 | 10.7 | 7.58 | 44.8367 | YES | 160
29 | 0.93 | 241 | 224.13 | 10.4 | 7.71 | 47.8336 | YES | 172
30 | 0.92 | 241 | 221.72 | 12 | 7.6 | 41.3565 | YES | 164
31 | 1.09 | 241 | 262.69 | 9.9 | 7.93 | 54.4892 | YES | 172
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2