## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-04-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.151 |  | 0.16 |  | 0.1 | 0.06 | 0.16
2 | 0.03 | 0.047 | 0.043 | 0.033 | 0.029 | 0.033 | 0.05
3 |  | 0.05 | 0.044 | 0.073 | 0.068 | 0.045 | 0.07
4 | 0.081 | 0.022 | 0.065 | 0.106 | 0.078 | 0.063 | 0.11
5 | 0.062 | 0.11 | 0.111 | 0.086 | 0.058 | 0.041 | 0.11
6 |  |  |  | 0.038 | 0.028 | 0.029 | 0.04
7 |  |  |  | 0.025 | 0.028 |  | 0.03
8 | [6 empty] | off
9 |  |  |  | 0.087 | 0.086 | 0.135 | 0.14
10 | 0.152 | 0.205 | 0.171 | 0.141 | 0.141 | 0.112 | 0.21
11 |  |  |  | 0.11 | 0.061 | 0.048 | 0.11
12 | 0.062 | 0.075 | 0.081 | 0.07 | 0.063 | 0.063 | 0.08
13 | 0.071 |  | 0.062 | 0.049 | 0.051 | 0.058 | 0.07
14 | 0.089 | 0.081 |  | 0.056 | 0.043 | 0.039 | 0.09
15 | 0.037 | 0.049 | 0.04 |  | 0.115 | 0.14 | 0.14
16 |  |  |  | 0.161 | 0.064 | 0.049 | 0.16
17 | 0.042 |  |  | 0.069 | 0.054 | 0.039 | 0.07
18 | 0.036 |  |  | 0.037 | 0.096 |  | 0.1
19 | 0.051 |  |  |  | 0.049 | 0.049 | 0.05
20 | 0.049 |  |  |  | 0.031 | 0.026 | 0.05
21 | 0.031 |  |  | 0.026 | 0.036 | 0.028 | 0.04
22 | 0.026 |  |  | 0.025 | 0.024 |  | 0.03
23 |  |  |  | 0.031 | 0.025 | 0.028 | 0.03
24 |  |  |  | 0.034 | 0.024 | 0.029 | 0.03
25 |  |  |  | 0.024 | 0.019 | 0.028 | 0.03
26 |  |  |  | 0.024 | 0.023 | 0.031 | 0.03
27 |  |  |  | 0.026 | 0.04 | 0.024 | 0.04
28 |  |  |  | 0.03 | 0.022 |  | 0.03
29 |  |  |  | 0.034 | 0.036 | 0.023 | 0.04
30 |  |  |  | 0.025 | 0.024 | 0.03 | 0.03
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | YES |  | YES
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 05/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.38 | 241 | 332.58 | 9.1 | 7.52 | 51.3343 | YES | 203
2 | 1.19 | 241 | 286.79 | 9.4 | 7.94 | 57.2186 | YES | 196
3 | 1.22 | 241 | 294.02 | 8.7 | 8.08 | 63.3382 | YES | 176
4 | 1.23 | 241 | 296.43 | 8.6 | 7.77 | 57.0741 | YES | 173
5 | 1.33 | 241 | 320.53 | 9.7 | 7.56 | 49.7377 | YES | 176
6 | 1.18 | 241 | 284.38 | 10.3 | 7.67 | 48.8474 | YES | 163
7 | 1.2 | 241 | 289.2 | 11 | 7.84 | 49.6363 | YES | 185
8 | 1.11 | 241 | 267.51 | 10.2 | 7.98 | 54.4917 | YES | 179
9 | 1.13 | 241 | 272.33 | 9.3 | 7.85 | 55.3856 | YES | 179
10 | 1.12 | 241 | 269.92 | 10.1 | 8.03 | 55.9187 | YES | 179
11 | 1.13 | 241 | 272.33 | 9.4 | 7.85 | 55.0136 | YES | 188
12 | 1 | 241 | 241 | 12.8 | 7.57 | 38.945 | YES | 159
13 | 1.18 | 241 | 284.38 | 11.2 | 7.93 | 50.4567 | YES | 174
14 | 1.31 | 241 | 315.71 | 10.7 | 8.37 | 62.0557 | YES | 169
15 | 1.26 | 241 | 303.66 | 10.3 | 8.29 | 61.5852 | YES | 180
16 | 1.31 | 241 | 315.71 | 10.4 | 8.22 | 59.9862 | YES | 189
17 | 1.29 | 241 | 310.89 | 11.3 | 8.35 | 59.012 | YES | 180
18 | 1.25 | 241 | 301.25 | 11.1 | 8.28 | 58.0548 | YES | 185
19 | 1.27 | 241 | 306.07 | 11.2 | 7.98 | 51.8977 | YES | 175
20 | 1.28 | 241 | 308.48 | 11.2 | 7.89 | 50.3155 | YES | 176
21 | 1.09 | 241 | 262.69 | 10.2 | 7.89 | 52.6416 | YES | 188
22 | 1.07 | 241 | 257.87 | 10.3 | 8.01 | 54.4601 | YES | 182
23 | 1.17 | 241 | 281.97 | 11.2 | 7.87 | 49.3341 | YES | 182
24 | 1.12 | 241 | 269.92 | 10.9 | 7.7 | 47.1141 | YES | 177
25 | 1.21 | 241 | 291.61 | 11 | 7.75 | 48.1293 | YES | 183
26 | 1.05 | 241 | 253.05 | 11.8 | 7.82 | 45.9399 | YES | 173
27 | 1.16 | 241 | 279.56 | 12.1 | 7.95 | 47.7469 | YES | 164
28 | 1.09 | 241 | 262.69 | 11.2 | 7.99 | 51.0189 | YES | 183
29 | 1.18 | 241 | 284.38 | 11.9 | 8.03 | 49.8963 | YES | 184
30 | 1.17 | 241 | 281.97 | 10.7 | 8 | 53.4366 | YES | 175
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2