## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-05-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.027 | 0.028 | 0.024 | 0.03
2 |  |  |  | 0.025 | 0.022 | 0.032 | 0.03
3 |  |  |  | 0.025 | 0.022 | 0.023 | 0.03
4 | 0.028 |  |  |  | 0.026 | 0.023 | 0.03
5 | 0.024 |  |  | 0.029 | 0.026 | 0.024 | 0.03
6 | 0.03 |  |  | 0.0252 | 0.026 | 0.02 | 0.03
7 | 0.024 |  |  | 0.03 | 0.029 | 0.024 | 0.03
8 |  |  |  | 0.023 | 0.034 | 0.027 | 0.03
9 |  |  |  | 0.034 | 0.025 |  | 0.03
10 | 0.025 |  |  | 0.025 | 0.025 | 0.03 | 0.03
11 | 0.025 |  |  | 0.023 | 0.022 | 0.022 | 0.03
12 | 0.023 |  |  | 0.023 | 0.0274 | 0.031 | 0.03
13 | 0.027 |  |  | 0.023 | 0.023 | 0.028 | 0.03
14 |  |  |  | 0.022 | 0.028 | 0.028 | 0.03
15 |  |  |  | 0.025 | 0.023 | 0.026 | 0.03
16 | 0.023 |  |  | 0.033 | 0.027 | 0.027 | 0.03
17 |  |  |  | 0.035 | 0.025 | 0.022 | 0.04
18 | [6 empty] | printer malfunction
19 |  |  |  | 0.036 | 0.042 | 0.032 | 0.04
20 |  |  |  | 0.037 | 0.06 |  | 0.06
21 |  |  | 0.028 | 0.029 | 0.027 | 0.028 | 0.03
22 |  |  | 0.027 | 0.025 | 0.024 |  | 0.03
23 |  |  |  | 0.039 | 0.026 |  | 0.04
24 |  |  |  | 0.025 | 0.025 | 0.024 | 0.03
25 |  |  |  | 0.045 | 0.024 | 0.026 | 0.05
26 |  |  |  | 0.025 | 0.026 | 0.026 | 0.03
27 |  |  |  | 0.033 | 0.027 | 0.024 | 0.03
28 |  |  |  | 0.024 | 0.027 | 0.023 | 0.03
29 |  |  |  | 0.029 | 0.027 | 0.03 | 0.03
30 |  |  |  | 0.026 | 0.022 | 0.039 | 0.04
31 |  |  |  | 0.03 | 0.028 | 0.024 | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | YES |  | YES
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE 6-6-2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.25 | 241 | 301.25 | 12 | 7.95 | 48.5615 | YES | 196
2 | 1.3 | 241 | 313.3 | 12.1 | 7.86 | 46.9917 | YES | 189
3 | 1.13 | 241 | 272.33 | 11.8 | 7.72 | 44.7519 | YES | 185
4 | 1.09 | 241 | 262.69 | 11.8 | 7.86 | 46.8061 | YES | 194
5 | 1.15 | 241 | 277.15 | 11.4 | 7.92 | 49.4402 | YES | 204
6 | 1.06 | 241 | 255.46 | 11.8 | 7.89 | 47.1446 | YES | 206
7 | 1.25 | 241 | 301.25 | 12.5 | 8.01 | 48.0449 | YES | 199
8 | 1.31 | 241 | 315.71 | 11.7 | 8.14 | 53.3855 | YES | 193
9 | 1.28 | 241 | 308.48 | 12.1 | 8.14 | 51.7924 | YES | 203
10 | 1.26 | 241 | 303.66 | 10.5 | 8.12 | 57.1376 | YES | 186
11 | 1.22 | 241 | 294.02 | 12 | 8.11 | 51.2313 | YES | 186
12 | 1.18 | 241 | 284.38 | 11.5 | 7.88 | 48.5846 | YES | 211
13 | 1.08 | 241 | 260.28 | 11.6 | 7.87 | 47.5464 | YES | 198
14 | 1.19 | 241 | 286.79 | 11.5 | 7.93 | 49.5121 | YES | 203
15 | 1.19 | 241 | 286.79 | 11.1 | 7.89 | 50.1339 | YES | 214
16 | 1.24 | 241 | 298.84 | 12.1 | 7.91 | 47.5057 | YES | 88
17 | 1.12 | 241 | 269.92 | 11.2 | 7.82 | 48.1899 | YES | 68
18 | 0.98 | 241 | 236.18 | 11.4 | 7.92 | 48.4898 | YES | 60
19 | 1.14 | 241 | 274.74 | 11.1 | 7.93 | 50.5632 | YES | print malfunction
20 | 1.24 | 241 | 298.84 | 11.1 | 8.05 | 53.3874 | YES | 88
21 | 1.24 | 241 | 298.84 | 11.6 | 8.13 | 53.1237 | YES | 99
22 | 0.87 | 241 | 209.67 | 12.3 | 7.87 | 44.3227 | YES | 90
23 | 0.91 | 241 | 219.31 | 13 | 7.24 | 33.6773 | YES | 54
24 | 0.98 | 241 | 236.18 | 12.8 | 7.65 | 40.0193 | YES | 56
25 | 0.98 | 241 | 236.18 | 13.1 | 7.66 | 39.3756 | YES | 60
26 | 0.99 | 241 | 238.59 | 13 | 7.74 | 40.8693 | YES | 60
27 | 0.97 | 241 | 233.77 | 13.4 | 7.82 | 40.8968 | YES | 86
28 | 1.18 | 241 | 284.38 | 14.5 | 7.88 | 39.8047 | YES | 88
29 | 0.97 | 241 | 233.77 | 15.2 | 7.74 | 35.2347 | YES | 134
30 | 1.1 | 241 | 265.1 | 12.8 | 7.89 | 44.3122 | YES | 141
31 | 0.89 | 241 | 214.49 | 13.7 | 7.86 | 40.3193 | YES | 148
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2