## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-06-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.026 | 0.03 | 0.023 | 0.03
2 | 0.027 |  |  | 0.026 | 0.024 | 0.031 | 0.03
3 | 0.024 |  |  | 0.024 | 0.022 | 0.025 | 0.03
4 | 0.022 |  |  | 0.028 | 0.023 | 0.028 | 0.03
5 |  |  |  | 0.026 | 0.026 | 0.026 | 0.03
6 |  |  |  | 0.025 | 0.027 |  | 0.03
7 |  |  |  | 0.026 | 0.027 | 0.024 | 0.03
8 | 0.026 | 0.022 | 0.023 | 0.025 |  | 0.025 | 0.03
9 | 0.024 |  |  |  | 0.025 | 0.024 | 0.03
10 | 0.022 | 0.025 |  |  | 0.027 |  | 0.03
11 | 0.021 | 0.022 |  | 0.028 | 0.024 | 0.022 | 0.03
12 | 0.023 | 0.028 |  | 0.025 | 0.023 | 0.026 | 0.03
13 | 0.027 | 0.024 |  | 0.027 | 0.026 | 0.025 | 0.03
14 | 0.025 |  |  | 0.024 | 0.023 | 0.023 | 0.03
15 |  |  |  | 0.023 | 0.024 | 0.024 | 0.02
16 | 0.024 | 0.021 | 0.023 | 0.025 | 0.021 | 0.021 | 0.03
17 |  |  |  | 0.027 | 0.025 | 0.022 | 0.03
18 | 0.022 | 0.027 |  | 0.027 | 0.025 | 0.024 | 0.03
19 |  |  |  | 0.027 | 0.024 | 0.025 | 0.03
20 |  |  |  | 0.031 |  |  | 0.03
21 |  | 0.03 | 0.032 | 0.029 |  |  | 0.03
22 | off | off | off | off | off | off | off
23 | 0.033 | 0.034 | 0.031 |  |  | 0.025 | 0.03
24 | 0.028 | 0.028 | 0.032 | 0.025 |  |  | 0.03
25 | 0.033 | 0.025 |  | 0.026 | 0.024 | 0.024 | 0.03
26 |  |  |  | 0.027 | 0.028 | 0.032 | 0.03
27 |  |  |  | 0.03 | 0.025 | 0.025 | 0.03
28 |  |  |  | 0.026 | 0.027 | 0.022 | 0.03
29 | 0.025 |  |  | 0.027 | 0.029 | 0.027 | 0.03
30 | 0.026 | 0.034 |  | 0.027 | 0.023 | 0.025 | 0.03
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | YES |  | YES
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 07/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-06-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.12 | 241 | 269.92 | 13.4 | 7.88 | 42.5258 | YES | 128
2 | 1.12 | 241 | 269.92 | 13.2 | 7.96 | 44.3795 | YES | 142
3 | 1.19 | 241 | 286.79 | 14.1 | 7.91 | 41.3754 | YES | 161
4 | 1.18 | 241 | 284.38 | 13.4 | 7.85 | 42.3454 | YES | 139
5 | 1.17 | 241 | 281.97 | 13.1 | 7.87 | 43.4651 | YES | 143
6 | 1.18 | 241 | 284.38 | 13.1 | 7.86 | 43.3545 | YES | 142
7 | 1.13 | 241 | 272.33 | 13.5 | 7.88 | 42.2928 | YES | 134
8 | 1.18 | 241 | 284.38 | 14.5 | 7.85 | 39.3671 | YES | 148
9 | 0.83 | 241 | 200.03 | 16.4 | 7.83 | 33.0996 | YES | 142
10 | 1.02 | 241 | 245.82 | 15.3 | 7.77 | 35.5927 | YES | 148
11 | 1.02 | 241 | 245.82 | 13.2 | 7.71 | 40.0234 | YES | 154
12 | 1.15 | 241 | 277.15 | 15.9 | 7.96 | 37.2312 | YES | 151
13 | 1.13 | 241 | 272.33 | 13.8 | 8 | 43.332 | YES | 145
14 | 1.14 | 241 | 274.74 | 12.9 | 8.14 | 48.4729 | YES | 128
15 | 1.22 | 241 | 294.02 | 15.5 | 7.87 | 37.2799 | YES | 129
16 | 1.08 | 241 | 260.28 | 11.2 | 8.04 | 51.8781 | YES | 155
17 | 1.25 | 241 | 301.25 | 14 | 7.84 | 40.8676 | YES | 132
18 | 1.22 | 241 | 294.02 | 13.4 | 7.87 | 42.8517 | YES | 129
19 | 1.33 | 241 | 320.53 | 13.7 | 7.82 | 41.759 | YES | 129
20 | 1.66 | 241 | 400.06 | 13.3 | 7.99 | 47.3796 | YES | 132
21 | 1.28 | 241 | 308.48 | 13.4 | 7.92 | 43.9441 | YES | 114
22 | 1.27 | 241 | 306.07 | 13.3 | 7.89 | 43.7013 | YES | 120
23 | 1.21 | 241 | 291.61 | 13.4 | 8.04 | 45.564 | YES | off
24 | 1.2 | 241 | 289.2 | 13.5 | 8.04 | 45.2124 | YES | 172
25 | 1.21 | 241 | 291.61 | 12.9 | 8.04 | 47.0961 | YES | 137
26 | 1.22 | 241 | 294.02 | 14.1 | 8.04 | 43.5502 | YES | 135
27 | 1.11 | 241 | 267.51 | 13.9 | 7.99 | 42.791 | YES | 133
28 | 1.08 | 241 | 260.28 | 14.5 | 7.68 | 36.5581 | YES | 132
29 | 1.1 | 241 | 265.1 | 14.5 | 7.79 | 38.1585 | YES | 145
30 | 1.18 | 241 | 284.38 | 15.3 | 7.94 | 38.5907 | YES | 152
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2