## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-08-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.024 | 0.024 |  | 0.025 | 0.022 | 0.022 | 0.03
2 | 0.022 |  |  | 0.023 | 0.021 | 0.025 | 0.03
3 |  |  | 0.026 | 0.023 | 0.026 | 0.021 | 0.03
4 |  |  |  | 0.027 | 0.025 | 0.033 | 0.03
5 | 0.026 |  | 0.024 | 0.024 | 0.028 | 0.023 | 0.03
6 | 0.023 | 0.024 | 0.022 | 0.023 | 0.021 | 0.026 | 0.03
7 |  |  |  | 0.029 |  | 0.026 | 0.03
8 | 0.026 |  |  | 0.027 | 0.023 | 0.023 | 0.03
9 | 0.022 | 0.022 |  | 0.026 | 0.024 | 0.025 | 0.03
10 | 0.024 | 0.023 | 0.027 | 0.026 | 0.026 | 0.029 | 0.03
11 | 0.025 |  |  | 0.026 | 0.022 |  | 0.03
12 | 0.021 | 0.025 | 0.028 | 0.025 | 0.022 | 0.022 | 0.03
13 |  |  |  | 0.038 | 0.025 | 0.025 | 0.04
14 | 0.028 |  |  | 0.024 | 0.022 | 0.023 | 0.03
15 | 0.025 |  |  | 0.026 | 0.022 | 0.026 | 0.03
16 | [6 empty] | off
17 |  |  |  |  | 0.034 | 0.031 | 0.03
18 | 0.03 | 0.025 | 0.026 | 0.026 |  | 0.026 | 0.03
19 | 0.025 | 0.028 | 0.023 | 0.024 | 0.023 | 0.023 | 0.03
20 | 0.026 | 0.024 | 0.027 | 0.027 | 0.027 | 0.024 | 0.03
21 | 0.024 |  |  | 0.034 | 0.03 | 0.026 | 0.03
22 | 0.022 | 0.028 | 0.03 | 0.027 | 0.027 | 0.026 | 0.03
23 | 0.025 | 0.027 | 0.024 |  | 0.022 | 0.019 | 0.03
24 | 0.027 | 0.022 |  |  |  |  | 0.03
25 | [6 empty] | off
26 |  |  |  | 0.031 | 0.037 | 0.028 | 0.04
27 | 0.024 | 0.027 | 0.023 | 0.022 | 0.026 | 0.023 | 0.03
28 | 0.025 | 0.031 | 0.024 | 0.022 | 0.021 | 0.036 | 0.04
29 | 0.027 | 0.024 | 0.023 | 0.023 | 0.02 | 0.028 | 0.03
30 |  |  |  | 0.024 | 0.025 | 0.021 | 0.03
31 | 0.027 | 0.022 |  |  | 0.027 | 0.03 | 0.03
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | #VALUE! |  |  | 2025-09-08
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.21 | 241 | 291.61 | 14.5 | 7.9 | 40.2355 | YES | 137
2 | 1.09 | 241 | 262.69 | 15.1 | 7.85 | 37.446 | YES | 133
3 | 1.17 | 241 | 281.97 | 15.2 | 7.9 | 38.2357 | YES | 190
4 | 0.93 | 241 | 224.13 | 14.6 | 7.81 | 37.4575 | YES | 132
5 | 0.95 | 241 | 228.95 | 14.7 | 7.88 | 38.2693 | YES | 130
6 | 0.88 | 241 | 212.08 | 16.6 | 7.88 | 33.4611 | YES | 135
7 | 0.97 | 241 | 233.77 | 15.3 | 7.95 | 37.822 | YES | 149
8 | 1.01 | 241 | 243.41 | 15.4 | 7.99 | 38.3033 | YES | 208
9 | 0.75 | 241 | 180.75 | 15.9 | 7.77 | 33.1662 | YES | 134
10 | 1.06 | 241 | 255.46 | 16.3 | 7.79 | 33.7015 | YES | 122
11 | 0.75 | 241 | 180.75 | 18 | 7.72 | 28.2999 | YES | 171
12 | 1.1 | 241 | 265.1 | 15.4 | 8.08 | 40.0009 | YES | 137
13 | 0.94 | 241 | 226.54 | 16.2 | 7.76 | 33.0976 | YES | didn't print
14 | 0.86 | 241 | 207.26 | 16.1 | 7.7 | 32.292 | YES | 178
15 | 0.96 | 241 | 231.36 | 16.4 | 7.68 | 31.7789 | YES | 181
16 | 0.99 | 241 | 238.59 | 16.3 | 7.72 | 32.5797 | YES | 175
17 | 1.03 | 241 | 248.23 | 16.1 | 7.67 | 32.5593 | YES | 187
18 | 1.12 | 241 | 269.92 | 15.9 | 7.62 | 32.7246 | YES | 142
19 | 0.95 | 241 | 228.95 | 16.6 | 7.61 | 30.5203 | YES | 146
20 | 0.98 | 241 | 236.18 | 16.8 | 7.68 | 31.0129 | YES | 128
21 | 0.7 | 241 | 168.7 | 17.3 | 7.57 | 27.8894 | YES | 177
22 | 0.81 | 241 | 195.21 | 16 | 7.62 | 31.3801 | YES | 202
23 | 0.95 | 241 | 228.95 | 15.5 | 7.57 | 32.3603 | YES | 137
24 | 0.86 | 241 | 207.26 | 16.7 | 7.49 | 28.701 | YES | 149
25 | 0.94 | 241 | 226.54 | 14.9 | 7.72 | 35.5588 | YES | 166
26 | 1.04 | 241 | 250.64 | 17.2 | 7.39 | 27.3002 | YES | 129
27 | 0.99 | 241 | 238.59 | 15.7 | 7.57 | 32.0775 | YES | 139
28 | 1.06 | 241 | 255.46 | 14.8 | 7.7 | 36.02 | YES | 186
29 | 1.06 | 241 | 255.46 | 15.1 | 7.71 | 35.4393 | YES | 181
30 | 1.03 | 241 | 248.23 | 15.2 | 7.62 | 33.937 | YES | 145
31 | 0.96 | 241 | 231.36 | 15 | 7.61 | 33.9934 | YES | 153
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2