## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-09-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.028 | 0.033 |  |  | 0.024 | 0.023 | 0.033
2 | 0.024 | 0.022 | 0.024 | 0.023 | 0.023 | 0.02 | 0.02
3 | 0.021 |  |  | 0.026 | 0.022 | 0.024 | 0.03
4 | 0.021 | 0.022 | 0.025 | 0.024 |  |  | 0.03
5 | 0.023 | 0.021 | 0.024 | 0.021 | 0.021 | 0.021 | 0.02
6 |  |  |  | 0.022 | 0.022 | 0.023 | 0.02
7 | 0.023 |  |  |  | 0.023 | 0.025 | 0.03
8 | 0.022 | 0.021 |  | 0.022 | 0.035 | 0.019 | 0.04
9 |  |  |  | 0.024 | 0.02 | 0.02 | 0.02
10 | 0.022 |  |  | 0.021 | 0.02 | 0.021 | 0.02
11 |  |  |  | 0.021 | 0.023 | 0.021 | 0.02
12 | 0.021 |  |  | 0.034 | 0.03 | 0.024 | 0.03
13 |  |  |  | 0.025 | 0.021 | 0.02 | 0.03
14 | 0.034 | 0.021 |  | 0.023 | 0.025 | 0.047 | 0.05
15 |  |  |  | 0.025 | 0.023 | 0.022 | 0.03
16 | 0.023 |  |  | 0.031 | 0.023 | 0.023 | 0.03
17 | 0.02 |  |  | 0.019 | 0.021 | 0.031 | 0.03
18 | [6 empty] | didn't print
19 | 0.019 |  |  | 0.022 | 0.035 | 0.029 | 0.04
20 |  |  |  | 0.021 | 0.021 | 0.019 | 0.02
21 | 0.027 |  |  |  | 0.041 | 0.038 | 0.04
22 | 0.025 |  |  | 0.026 |  |  | 0.03
23 |  |  | 0.022 | 0.021 | 0.021 | 0.022 | 0.02
24 |  |  |  | 0.018 | 0.018 | 0.02 | 0.02
25 |  |  | 0.023 |  |  |  | 0.02
26 |  |  |  | 0.021 | 0.02 | 0.022 | 0.02
27 | 0.022 | 0.029 | 0.019 | 0.015 | 0.013 |  | 0.03
28 |  |  |  | 0.014 | 0.013 | 0.018 | 0.02
29 | 0.02 |  | 0.015 |  | 0.124 | 0.072 | 0.12
30 |  |  |  | 0.019 | 0.017 | 0.019 | 0.02
31
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: Temperature on September 1 was unavailable due to a sensor malfunction. Worst case scenario temperature of 5 degrees C was used. CT met. |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | Date: 10/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.84 | 241 | 202.44 | 5 | 7.96 | 74.7057 | YES | 127
2 | 1.38 | 241 | 332.58 | 14.7 | 8.04 | 42.6178 | YES | 140
3 | 0.32 | 241 | 77.12 | 15.8 | 8.14 | 36.4536 | YES | 183
4 | 1.32 | 241 | 318.12 | 15.1 | 8.01 | 40.7693 | YES | 144
5 | 0.88 | 241 | 212.08 | 15.7 | 8.04 | 37.687 | YES | 149
6 | 0.91 | 241 | 219.31 | 15.9 | 8.24 | 40.1715 | YES | 137
7 | 0.98 | 241 | 236.18 | 17 | 8.04 | 34.9621 | YES | 133
8 | 1.08 | 241 | 260.28 | 15.6 | 8.13 | 40.1166 | YES | 150
9 | 1.02 | 241 | 245.82 | 15.5 | 8.06 | 39.0888 | YES | 143
10 | 1.03 | 241 | 248.23 | 15.9 | 8.03 | 37.6886 | YES | 143
11 | 1.02 | 241 | 245.82 | 15.6 | 8.04 | 38.5451 | YES | 143
12 | 0.95 | 241 | 228.95 | 15.6 | 8.06 | 38.5234 | YES | 147
13 | 1.1 | 241 | 265.1 | 16.2 | 8.08 | 37.9327 | YES | 133
14 | 1.07 | 241 | 257.87 | 15.7 | 8.05 | 38.6499 | YES | 130
15 | 1.03 | 241 | 248.23 | 15.2 | 8.15 | 41.265 | YES | 138
16 | 1 | 241 | 241 | 15.9 | 8.13 | 38.9713 | YES | 182
17 | 0.99 | 241 | 238.59 | 15.9 | 8.08 | 38.2162 | YES | 140
18 | 0.99 | 241 | 238.59 | 15.7 | 7.94 | 36.7781 | YES | 139
19 | 1.14 | 241 | 274.74 | 17.3 | 7.87 | 32.7739 | YES
20 | 0.82 | 241 | 197.62 | 15.4 | 7.77 | 34.5626 | YES | 134
21 | 0.98 | 241 | 236.18 | 15.8 | 7.67 | 33.0281 | YES | 126
22 | 0.94 | 241 | 226.54 | 14.5 | 7.83 | 38.0293 | YES | 147
23 | 0.95 | 241 | 228.95 | 15.5 | 7.86 | 36.0219 | YES | 154
24 | 0.99 | 241 | 238.59 | 14.6 | 7.81 | 37.7132 | YES | 135
25 | 1.01 | 241 | 243.41 | 14.1 | 7.83 | 39.3635 | YES | 142
26 | 1.04 | 241 | 250.64 | 16 | 8.04 | 37.6201 | YES | 136
27 | 0.93 | 241 | 224.13 | 14.1 | 7.7 | 37.1825 | YES | 139
28 | 1.04 | 241 | 250.64 | 16 | 7.87 | 35.3322 | YES | 120
29 | 1.02 | 241 | 245.82 | 14.2 | 7.91 | 40.3185 | YES | 152
30 | 0.94 | 241 | 226.54 | 14.1 | 7.81 | 38.7657 | YES | 146
31 |  | 241
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2