## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-10-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | [6 empty] | printer malfunction
2 | [6 empty] | printer malfunction
3 | [6 empty] | printer malfunction
4 | [6 empty] | printer malfunction
5 | [6 empty] | printer malfunction
6 |  |  |  | 0.25 | 0.022 | 0.02 | 0.25
7 |  |  |  | 0.023 | 0.024 | 0.023 | 0.02
8 |  |  |  | 0.023 | 0.026 |  | 0.03
9 |  |  |  | 0.027 | 0.023 | 0.022 | 0.03
10 |  |  |  | 0.021 | 0.025 | 0.022 | 0.03
11 |  |  |  | 0.024 | 0.021 | 0.021 | 0.02
12 | 0.022 |  |  | 0.023 | 0.024 |  | 0.02
13 |  |  |  | 0.043 | 0.025 | 0.028 | 0.04
14 |  |  |  | 0.034 | 0.028 |  | 0.03
15 |  |  |  | 0.026 | 0.029 |  | 0.03
16 |  |  |  |  | 0.029 | 0.029 | 0.03
17 |  |  |  | 0.045 | 0.026 | 0.023 | 0.05
18 |  |  |  | 0.037 | 0.025 | 0.024 | 0.04
19 |  |  | 0.053 |  |  |  | 0.052
20 | [6 empty] | off
21 |  |  |  | 0.036 | 0.035 |  | 0.04
22 | 0.043 | 0.035 | 0.064 | 0.03 | 0.027 | 0.031 | 0.06
23 |  |  |  | 0.037 | 0.021 | 0.03 | 0.04
24 | [6 empty] | off
25 |  |  |  |  | 0.029 | 0.031 | 0.03
26 |  | 0.11 | 0.064 | 0.023 | 0.034 | 0.027 | 0.11
27 | 0.052 | 0.033 | 0.236 |  |  | 0.21 | 0.24
28 | 0.084 | 0.168 | 0.198 | 0.159 | 0.037 | 0.029 | 0.2
29 | 0.026 | 0.034 | 0.03 | 0.028 |  |  | 0.03
30 |  | 0.026 | 0.024 | 0.035 | 0.03 |  | 0.04
31 |  |  |  | 0.045 | 0.108 | 0.024 | 0.11
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | #VALUE! |  |  | 2025-11-09
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-10-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.86 | 241 | 207.26 | 13.9 | 7.76 | 38.2182 | YES | printer malfunction
2 | 0.94 | 241 | 226.54 | 14.8 | 7.77 | 36.4629 | YES | printer malfunction
3 | 1.08 | 241 | 260.28 | 15.3 | 7.73 | 35.3105 | YES | printer malfunction
4 | 1.1 | 241 | 265.1 | 15.4 | 7.79 | 35.9439 | YES | printer malfunction
5 | 1.21 | 241 | 291.61 | 13.4 | 7.75 | 40.954 | YES | printer malfunction
6 | 1.23 | 241 | 296.43 | 13.1 | 7.72 | 41.4113 | YES | printer malfunction
7 | 1 | 241 | 241 | 13.4 | 7.7 | 39.2616 | YES | 129
8 | 0.99 | 241 | 238.59 | 13.2 | 7.68 | 39.4492 | YES | 138
9 | 1.09 | 241 | 262.69 | 12.6 | 7.79 | 43.2328 | YES | 137
10 | 1.11 | 241 | 267.51 | 12.8 | 7.75 | 42.1358 | YES | 107
11 | 1.08 | 241 | 260.28 | 13.2 | 7.65 | 39.4154 | YES | 118
12 | 1.15 | 241 | 277.15 | 12.8 | 7.56 | 39.4669 | YES | 123
13 | 1.18 | 241 | 284.38 | 12.3 | 7.58 | 41.4613 | YES | 136
14 | 1.14 | 241 | 274.74 | 12 | 7.96 | 48.1266 | YES | 141
15 | 1.05 | 241 | 253.05 | 11.7 | 7.99 | 49.1172 | YES | 134
16 | 1.19 | 241 | 286.79 | 11.1 | 8.03 | 52.7027 | YES | 139
17 | 1.09 | 241 | 262.69 | 11.5 | 8.07 | 51.4522 | YES | 133
18 | 1.04 | 241 | 250.64 | 11.7 | 8 | 49.2359 | YES | 125
19 | 1.09 | 241 | 262.69 | 11 | 8.02 | 52.2641 | YES | 123
20 | 1.12 | 241 | 269.92 | 10 | 8 | 55.6934 | YES | 122
21 | 0.96 | 241 | 231.36 | 12.6 | 8.01 | 46.1906 | YES | 127
22 | 0.97 | 241 | 233.77 | 11.4 | 8.08 | 51.2727 | YES | 138
23 | 0.83 | 241 | 200.03 | 11.9 | 8.09 | 48.9739 | YES | 138
24 | 0.87 | 241 | 209.67 | 11.8 | 7.92 | 46.6294 | YES | 136
25 | 0.79 | 241 | 190.39 | 11.2 | 7.86 | 47.0751 | YES | 113
26 | 0.91 | 241 | 219.31 | 10.8 | 7.84 | 48.664 | YES | 147
27 | 1.1 | 241 | 265.1 | 10.2 | 7.8 | 51.0348 | YES | 123
28 | 1.2 | 241 | 289.2 | 10.4 | 7.76 | 50.2156 | YES | 133
29 | 1.13 | 241 | 272.33 | 10.6 | 7.72 | 48.461 | YES | 135
30 | 0.95 | 241 | 228.95 | 10.6 | 7.73 | 47.6456 | YES | 124
31 | 1.04 | 241 | 250.64 | 11.3 | 7.68 | 45.1464 | YES | 107
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2