## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-11-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.057 |  | 0.083 | 0.031 |  | 0.08
2 | off | off | off | off | off | off | off
3 |  |  | 0.027 | 0.2 | 0.024 | 0.026 | 0.03
4 | 0.025 | 0.024 | 0.029 | 0.025 | 0.029 | 0.026 | 0.03
5 | 0.024 | 0.06 | 0.143 | 0.034 | 0.024 |  | 0.14
6 |  |  |  | 0.084 | 0.128 |  | 0.08
7 |  |  |  | 0.186 | 0.02 | 0.02 | 0.19
8 | [6 empty] | printer malfunction
9 |  |  |  | 0.186 | 0.02 | 0.02 | 0.19
10 | 0.019 | 0.023 | 0.062 | 0.016 | 0.026 | 0.026 | 0.06
11 | 0.071 |  | 0.019 | 0.018 | 0.019 |  | 0.07
12 | 0.021 | 0.022 | 0.024 | 0.02 | 0.021 | 0.022 | 0.02
13 | 0.023 | 0.023 | 0.045 | 0.259 | 0.031 | 0.026 | 0.26
14 | 0.054 |  |  | 0.023 | 0.021 | 0.074 | 0.07
15 |  |  |  | 0.025 | 0.025 | 0.025 | 0.03
16 | 0.025 |  |  |  | 0.021 | 0.023 | 0.03
17 | 0.023 | 0.029 | 0.059 | 0.028 | 0.028 |  | 0.06
18 |  |  |  | 0.023 | 0.022 | 0.022 | 0.02
19 | 0.022 | 0.023 |  | 0.025 | 0.027 | 0.023 | 0.03
20 |  |  |  | 0.025 | 0.023 | 0.023 | 0.03
21 | 0.022 | 0.025 | 0.024 |  | 0.024 | 0.02 | 0.03
22 | 0.023 |  | 0.02 | 0.024 |  |  | 0.02
23 |  |  |  | 0.024 | 0.041 | 0.024 | 0.04
24 | 0.029 | 0.025 | 0.024 | 0.073 | 0.023 | 0.022 | 0.07
25 |  |  |  | 0.017 | 0.024 | 0.035 | 0.04
26 | off | off | off | off | off | off | off
27 |  |  |  | 0.027 | 0.019 | 0.038 | 0.04
28 |  |  |  | 0.129 | 0.029 | 0.086 | 0.13
29 | [6 empty] | printer malfunction
30 | 0.022 | 0.023 | 0.024 | 0.023 | 0.026 | 0.023 | 0.03
31
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | 2025-12-09
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-11-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.37 | 241 | 330.17 | 11.54 | 7.6 | 44.8452 | YES | 126
2 | 0.85 | 241 | 204.85 | 12 | 7.64 | 41.6102 | YES | 149
3 | 0.85 | 241 | 204.85 | 11.5 | 7.45 | 40.2379 | YES | 161
4 | 1.22 | 241 | 294.02 | 10.3 | 7.69 | 49.4212 | YES | 155
5 | 1.07 | 241 | 257.87 | 11.3 | 7.76 | 46.598 | YES | 123
6 | 1.06 | 241 | 255.46 | 11.5 | 7.66 | 44.3412 | YES | 127
7 | 1.13 | 241 | 272.33 | 11 | 7.76 | 47.8619 | YES | 124
8 | 1.12 | 241 | 269.92 | 10.9 | 7.86 | 49.8675 | YES | 158
9 | 1.14 | 241 | 274.74 | 11 | 8.03 | 52.7536 | YES
10 | 1.16 | 241 | 279.56 | 11.1 | 8.08 | 53.4696 | YES | 158
11 | 1.18 | 241 | 284.38 | 10.6 | 7.88 | 51.596 | YES | 143
12 | 1.16 | 241 | 279.56 | 10.5 | 7.93 | 52.7584 | YES | 146
13 | 1.28 | 241 | 308.48 | 11.6 | 7.89 | 48.9895 | YES | 126
14 | 1.18 | 241 | 284.38 | 11.5 | 7.96 | 49.9863 | YES | 134
15 | 1.06 | 241 | 255.46 | 11.1 | 7.89 | 49.3941 | YES | 121
16 | 1.24 | 241 | 298.84 | 11.9 | 7.4 | 40.2415 | YES | 122
17 | 1.18 | 241 | 284.38 | 11.9 | 7.36 | 39.4208 | YES | 158
18 | 1.26 | 241 | 303.66 | 9.8 | 7.09 | 41.5318 | YES | 132
19 | 0.91 | 241 | 219.31 | 10.1 | 7.24 | 41.2605 | YES | 131
20 | 0.98 | 241 | 236.18 | 9.9 | 7.12 | 40.4068 | YES | 138
21 | 1.08 | 241 | 260.28 | 10.1 | 7.15 | 40.7546 | YES | 180
22 | 1 | 241 | 241 | 9.8 | 7.38 | 44.6504 | YES | 131
23 | 0.91 | 241 | 219.31 | 11 | 7.42 | 41.4208 | YES | 114
24 | 1.01 | 241 | 243.41 | 10.7 | 7.63 | 45.9979 | YES | 132
25 | 1.14 | 241 | 274.74 | 8.8 | 7.73 | 54.9309 | YES | 147
26 | 0.98 | 241 | 236.18 | 8.7 | 7.45 | 49.1258 | YES | 134
27 | 0.99 | 241 | 238.59 | 9 | 7.48 | 48.7245 | YES | 119
28 | 1.03 | 241 | 248.23 | 12.4 | 8.11 | 48.8078 | YES | 114
29 | 0.95 | 241 | 228.95 | 9.7 | 8.44 | 65.3388 | YES | 140
30 | 0.97 | 241 | 233.77 | 9.5 | 8.25 | 61.9644 | YES
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2