## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-12-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.035 | 0.025 | 0.021 | 0.024 | 0.021 | 0.022 | 0.04
2 | 0.022 | 0.022 | 0.021 | 0.019 | 0.024 | 0.025 | 0.03
3 | 0.022 | 0.023 | 0.022 | 0.02 | 0.022 | 0.02 | 0.02
4 | 0.02 | 0.019 | 0.027 | 0.025 | 0.024 | 0.052 | 0.05
5 | 0.082 | 0.053 |  |  | 0.024 | 0.016 | 0.08
6 | 0.018 | 0.015 | 0.017 | 0.02 | 0.02 | 0.019 | 0.02
7 |  |  |  | 0.018 | 0.021 | 0.02 | 0.02
8 | 0.017 | 0.025 |  | 0.019 | 0.026 | 0.101 | 0.1
9 |  |  |  | 0.277 |  |  | 0.28
10 |  |  |  | 0.024 | 0.038 | 0.039 | 0.04
11 | 0.022 | 0.017 | 0.025 |  |  |  | 0.03
12 | [5 empty] | 0.019 | 0.02
13 | 0.017 | 0.023 | 0.021 | 0.075 | 0.021 |  | 0.08
14 |  |  |  | 0.018 | 0.022 | 0.021 | 0.02
15 | 0.022 | 0.023 |  |  |  |  | 0.02
16 |  |  |  | 0.204 | 0.023 | 0.023 | 0.2
17
18 |  |  |  |  | 0.247 | 0.027 | 0.25
19 | 0.031 | 0.049 |  | 0.276 |  |  | 0.28
20 | off | off | off | off | off | off | off
21 | [5 empty] | 0.148 | 0.15
22 |  |  | 0.191 |  | 0.228 | 0.023 | 0.23
23 | 0.087 | 0.022 | 0.021 |  | 0.025 | 0.027 | 0.09
24 | 0.028 | 0.033 | 0.032 | 0.029 | 0.055 | 0.104 | 0.1
25 | 0.041 | 0.036 | 0.027 | 0.029 | 0.046 | 0.048 | 0.05
26 | 0.054 |  |  | 0.122 |  |  | 0.12
27 |  |  |  |  | 0.288 |  | 0.29
28 | 0.277 |  |  |  |  | 0.204 | 0.28
29 | 0.204 |  |  | 0.184 | 0.209 |  | 0.21
30 |  |  |  | 0.193 | 0.152 |  | 0.19
31 |  |  |  | 0.152 | 0.075 | 0.112 | 0.15
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | 2026-01-08
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-12-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.98 | 241 | 236.18 | 7.9 | 7.93 | 61.5944 | YES | 197
2 | 1.09 | 241 | 262.69 | 9.3 | 7.83 | 54.7361 | YES | 160
3 | 1.28 | 241 | 308.48 | 10.2 | 7.78 | 51.7288 | YES | 156
4 | 1.23 | 241 | 296.43 | 9.5 | 7.82 | 54.6861 | YES | 161
5 | 1.24 | 241 | 298.84 | 10 | 7.87 | 53.8953 | YES | 129
6 | 1.26 | 241 | 303.66 | 10.9 | 7.91 | 51.5851 | YES | 116
7 | 1.31 | 241 | 315.71 | 10.7 | 7.95 | 53.3408 | YES | 124
8 | 1.27 | 241 | 306.07 | 11.3 | 7.87 | 49.5692 | YES | 143
9 | 1.31 | 241 | 315.71 | 11.6 | 7.72 | 46.2832 | YES | 129
10 | 1.23 | 241 | 296.43 | 11.3 | 7.56 | 44.2191 | YES | 127
11 | 1.04 | 241 | 250.64 | 11.1 | 7.546 | 43.6397 | YES | 128
12 | 0.94 | 241 | 226.54 | 12.3 | 7.62 | 40.9277 | YES | 124
13 | 1.04 | 241 | 250.64 | 11.5 | 7.57 | 42.8648 | YES | 117
14 | 1.17 | 241 | 281.97 | 11.7 | 7.48 | 41.5975 | YES | 116
15 | 1.33 | 241 | 320.53 | 13 | 7.61 | 40.4879 | YES | 158
16 | 1.33 | 241 | 320.53 | 11.4 | 7.59 | 44.8993 | YES | 143
17 | 1.44 | 241 | 347.04 | 10.6 | 7.81 | 51.8462 | YES | 135
18 | 1.44 | 241 | 347.04 | 9.4 | 7.75 | 55.0059 | YES
19 | 1.65 | 241 | 397.65 | 9.3 | 7.98 | 61.6518 | YES | 125
20 | 1.78 | 241 | 428.98 | 10.2 | 7.97 | 58.6696 | YES | 110
21 | 1.27 | 241 | 306.07 | 8.8 | 7.74 | 55.9622 | YES | 93
22 | 1.67 | 241 | 402.47 | 9.4 | 7.99 | 61.5996 | YES | 117
23 | 1.33 | 241 | 320.53 | 8.5 | 7.62 | 55.0761 | YES | 120
24 | 1.62 | 241 | 390.42 | 8.3 | 8.01 | 66.4909 | YES | 121
25 | 1.33 | 241 | 320.53 | 9 | 8.05 | 62.1784 | YES | 121
26 | 1.51 | 241 | 363.91 | 8.4 | 8.16 | 68.8567 | YES | 133
27 | 1.38 | 241 | 332.58 | 8.1 | 8.12 | 68.2195 | YES | 113
28 | 1.39 | 241 | 334.99 | 8.1 | 8.19 | 70.0679 | YES | 127
29 | 1.5 | 241 | 361.5 | 7 | 8.09 | 73.8004 | YES | 143
30 | 1.43 | 241 | 344.63 | 10.5 | 8.08 | 57.4394 | YES | 122
31 | 1.47 | 241 | 354.27 | 7.4 | 8.13 | 72.6012 | YES | 121
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2