## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-01-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.088 | 0.135 |  |  |  | 0.203 | 0.2
2 | 0.18 |  |  |  |  | 0.034 | 0.18
3 | 0.047 |  |  |  | 0.036 | 0.027 | 0.05
4 |  |  |  | 0.019 | 0.021 | 0.027 | 0.03
5 | 0.024 |  |  | 0.027 | 0.036 | 0.045 | 0.05
6 | 0.078 | 0.065 | 0.091 | 0.041 | 0.021 |  | 0.09
7 |  |  | 0.026 | 0.031 | 0.04 | 0.045 | 0.05
8 |  |  |  | 0.235 |  |  | 0.24
9 | [5 empty] | 0.027 | 0.03
10 | 0.031 | 0.024 | 0.022 | 0.025 |  |  | 0.03
11 |  |  | 0.034 | 0.07 | 0.066 |  | 0.047
12 |  |  |  | 0.038 | 0.058 | 0.041 | 0.06
13 |  |  |  | 0.043 |  | 0.024 | 0.04
14 |  |  |  | 0.03 | 0.03 | 0.032 | 0.03
15 |  |  |  | 0.057 | 0.048 |  | 0.06
16 |  |  |  | 0.052 | 0.059 | 0.065 | 0.07
17 |  |  |  | 0.08 | 0.138 | 0.086 | 0.14
18 |  |  |  | 0.213 | 0.065 | 0.064 | 0.21
19 |  |  |  | 0.059 | 0.143 | 0.108 | 0.14
20 |  |  |  | 0.132 | 0.143 | 0.164 | 0.16
21 |  |  |  | 0.021 | 0.024 | 0.02 | 0.02
22 |  |  |  | 0.018 | 0.033 | 0.02 | 0.03
23 |  |  |  | 0.026 | 0.02 | 0.02 | 0.03
24 |  |  |  |  | 0.021 | 0.021 | 0.02
25 | 0.026 |  |  | 0.018 | 0.02 |  | 0.03
26 |  |  |  | 0.022 | 0.021 | 0.021 | 0.02
27 |  |  |  | 0.035 | 0.021 | 0.019 | 0.04
28 |  |  |  | 0.023 | 0.021 | 0.021 | 0.02
29 |  |  |  | 0.021 | 0.026 | 0.024 | 0.03
30 |  |  |  | 0.033 | 0.021 | 0.024 | 0.03
31 |  |  |  | 0.037 | 0.024 | 0.024 | 0.04
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | 2026-02-10
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2026-01-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.24 | 241 | 298.84 | 8.3 | 7.81 | 59.1595 | YES | 129
2 | 1.21 | 241 | 291.61 | 9.2 | 7.83 | 55.8748 | YES | 125
3 | 1.3 | 241 | 313.3 | 10 | 7.85 | 53.8814 | YES | 123
4 | 1.23 | 241 | 296.43 | 9.8 | 7.77 | 52.6426 | YES | 121
5 | 1.24 | 241 | 298.84 | 9.7 | 7.81 | 53.8238 | YES | 137
6 | 1.23 | 241 | 296.43 | 9.6 | 7.88 | 55.5018 | YES | 162
7 | 1.22 | 241 | 294.02 | 8.7 | 7.98 | 61.0834 | YES | 135
8 | 1.22 | 241 | 294.02 | 8.5 | 8.01 | 62.5965 | YES | 137
9 | 1.31 | 241 | 315.71 | 7.8 | 7.83 | 62.1506 | YES | 126
10 | 1.32 | 241 | 318.12 | 7.3 | 7.82 | 64.1451 | YES | 123
11 | 1.23 | 241 | 296.43 | 7.6 | 7.75 | 60.6349 | YES | 122
12 | 1.27 | 241 | 306.07 | 10.1 | 8.12 | 58.7731 | YES | 134
13 | 1.23 | 241 | 296.43 | 9.1 | 8.27 | 66.1179 | YES | 151
14 | 1.23 | 241 | 296.43 | 8.8 | 8.12 | 63.903 | YES | 134
15 | 1.32 | 241 | 318.12 | 8.2 | 8.14 | 67.772 | YES | 144
16 | 1.17 | 241 | 281.97 | 8.5 | 8.03 | 62.6858 | YES | 130
17 | 1.36 | 241 | 327.76 | 9.4 | 8.07 | 61.1636 | YES | 129
18 | 1.32 | 241 | 318.12 | 8 | 8.1 | 67.711 | YES | 127
19 | 1.25 | 241 | 301.25 | 8.8 | 8.03 | 61.9944 | YES | 126
20 | 1.05 | 241 | 253.05 | 6.9 | 7.92 | 66.2386 | YES | 147
21 | 1.09 | 241 | 262.69 | 7.5 | 7.94 | 64.3449 | YES | 134
22 | 1.31 | 241 | 315.71 | 5.1 | 7.97 | 78.7153 | YES | 146
23 | 1.38 | 241 | 332.58 | 7.1 | 7.91 | 67.666 | YES | 143
24 | 1.28 | 241 | 308.48 | 9.3 | 7.64 | 52.2656 | YES | 133
25 | 0.97 | 241 | 233.77 | 6.2 | 7.74 | 64.4713 | YES | 118
26 | 1.49 | 241 | 359.09 | 7.7 | 7.65 | 59.8676 | YES | 141
27 | 1.31 | 241 | 315.71 | 6.3 | 7.74 | 66.6292 | YES | 141
28 | 1.26 | 241 | 303.66 | 6.9 | 7.7 | 62.6671 | YES | 143
29 | 1.27 | 241 | 306.07 | 8.4 | 7.71 | 56.8769 | YES | 147
30 | 1.33 | 241 | 320.53 | 8.6 | 7.71 | 56.5045 | YES | 146
31 | 1.36 | 241 | 327.76 | 9.1 | 7.75 | 55.6137 | YES | 133
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2