## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-02-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.058 | 0.075 | 0.032 | 0.08
2 | 0.032 |  |  |  | 0.028 |  | 0.03
3 | 0.036 |  |  | 0.035 | 0.026 |  | 0.04
4 |  |  |  | 0.024 | 0.021 | 0.046 | 0.05
5 |  |  |  | 0.025 | 0.025 |  | 0.03
6 |  |  |  | 0.041 | 0.023 | 0.023 | 0.04
7 |  |  |  |  | 0.029 | 0.033 | 0.03
8 |  |  |  |  | 0.023 | 0.039 | 0.04
9 | 0.019 |  |  | 0.025 |  |  | 0.03
10 |  |  |  | 0.105 | 0.023 | 0.022 | 0.11
11 | 0.022 | 0.024 | 0.024 | 0.023 |  |  | 0.02
12 | 0.021 | 0.023 |  | 0.02 | 0.018 |  | 0.02
13 |  |  |  | 0.019 | 0.029 | 0.025 | 0.03
14 |  |  |  | 0.024 | 0.031 | 0.02 | 0.03
15 | [6 empty] | printer malfunction
16 | [6 empty] | printer malfunction
17 |  |  |  | 0.02 | 0.025 |  | 0.03
18 |  |  |  | 0.017 | 0.019 | 0.029 | 0.03
19 |  |  |  | 0.022 | 0.027 | 0.023 | 0.03
20 |  |  |  | 0.02 | 0.019 | 0.02 | 0.02
21 |  |  |  | 0.023 | 0.018 | 0.02 | 0.02
22 |  |  |  |  | 0.025 | 0.02 | 0.03
23 |  |  |  | 0.029 | 0.025 | 0.022 | 0.03
24 |  |  |  | 0.03 | 0.029 | 0.025 | 0.03
25 |  |  |  | 0.021 | 0.024 |  | 0.02
26 |  |  |  | 0.024 | 0.021 |  | 0.02
27 |  |  |  | 0.035 | 0.035 | 0.031 | 0.04
28 |  |  |  | 0.034 | 0.026 | 0.024 | 0.03
29
30
31
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | 2026-03-11
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2026-02-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.32 | 241 | 318.12 | 9.4 | 7.76 | 54.445 | YES | 126
2 | 1.51 | 241 | 363.91 | 8.8 | 8.04 | 64.1349 | YES | 142
3 | 1.21 | 241 | 291.61 | 9.2 | 7.78 | 54.8802 | YES | 149
4 | 1.24 | 241 | 298.84 | 10.2 | 7.68 | 49.689 | YES | 141
5 | 1.21 | 241 | 291.61 | 10.7 | 7.73 | 48.7534 | YES | 147
6 | 1.19 | 241 | 286.79 | 9.9 | 7.85 | 53.5622 | YES | 141
7 | 1.21 | 241 | 291.61 | 9.7 | 7.8 | 53.4464 | YES | 129
8 | 1.24 | 241 | 298.84 | 9.2 | 7.83 | 56.0688 | YES | 128
9 | 1.08 | 241 | 260.28 | 9.4 | 7.69 | 51.6524 | YES | 139
10 | 1.32 | 241 | 318.12 | 8.4 | 7.78 | 58.6691 | YES | 131
11 | 1.2 | 241 | 289.2 | 8.3 | 7.81 | 58.8856 | YES | 146
12 | 1.21 | 241 | 291.61 | 8.7 | 7.7 | 55.1534 | YES | 144
13 | 1.17 | 241 | 281.97 | 8.6 | 7.68 | 54.8751 | YES | 151
14 | 1.14 | 241 | 274.74 | 8.7 | 7.71 | 54.9065 | YES | 127
15 | 1.21 | 241 | 291.61 | 9.2 | 7.77 | 54.6836 | YES | 130
16 | 1.21 | 241 | 291.61 | 8.3 | 7.68 | 56.2558 | YES
17 | 1.19 | 241 | 286.79 | 7.9 | 7.59 | 55.8253 | YES
18 | 1.2 | 241 | 289.2 | 7.4 | 7.7 | 60.152 | YES | 136
19 | 1.21 | 241 | 291.61 | 6.8 | 7.87 | 66.7273 | YES | 137
20 | 1.53 | 241 | 368.73 | 5.7 | 7.86 | 74.4419 | YES | 149
21 | 1.28 | 241 | 308.48 | 7.2 | 7.91 | 66.4224 | YES | 135
22 | 1.17 | 241 | 281.97 | 8.4 | 7.37 | 49.7828 | YES | 129
23 | 1.2 | 241 | 289.2 | 8.9 | 7.65 | 53.3874 | YES | 139
24 | 1.2 | 241 | 289.2 | 7.7 | 7.85 | 62.2277 | YES | 136
25 | 0.97 | 241 | 233.77 | 6.5 | 7.9 | 66.9507 | YES | 130
26 | 1.09 | 241 | 262.69 | 6.9 | 7.91 | 66.3075 | YES | 142
27 | 1.07 | 241 | 257.87 | 7.4 | 7.42 | 53.5736 | YES | 137
28 | 1.1 | 241 | 265.1 | 7.3 | 7.43 | 54.3162 | YES | 129
29 |  | 241
30 |  | 241
31 |  | 241
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2