## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | CLATSOP
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-03-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  |  | 0.025 | 0.019 | 0.03
2 |  |  |  | 0.025 | 0.025 | 0.021 | 0.03
3 |  |  |  | 0.022 | 0.02 | 0.019 | 0.02
4 |  |  |  | 0.026 | 0.045 | 0.046 | 0.05
5 |  |  |  | 0.038 | 0.03 | 0.024 | 0.04
6 |  |  |  | 0.02 | 0.02 | 0.023 | 0.02
7 |  |  |  | 0.024 | 0.022 | 0.019 | 0.02
8 |  |  |  |  | 0.04 | 0.022 | 0.04
9 |  |  |  |  | 0.018 | 0.045 | 0.05
10 |  |  |  |  | 0.023 | 0.02 | 0.02
11 |  |  |  | 0.053 |  |  | 0.05
12 |  |  |  |  | 0.042 | 0.019 | 0.04
13 | 0.062 | 0.028 |  | 0.026 |  |  | 0.06
14 |  |  | 0.045 | 0.018 | 0.018 | 0.022 | 0.05
15 |  |  |  | 0.023 | 0.031 | 0.032 | 0.03
16 |  |  |  | 0.022 | 0.021 | 0.021 | 0.02
17 |  |  |  | 0.033 | 0.022 | 0.02 | 0.03
18 |  |  |  | 0.026 | 0.028 | 0.019 | 0.03
19 |  |  |  | 0.022 | 0.025 |  | 0.03
20 |  |  |  | 0.024 | 0.022 |  | 0.02
21 |  |  |  | 0.023 | 0.025 | 0.027 | 0.03
22 |  |  |  | 0.024 | 0.016 | 0.022 | 0.02
23 |  |  |  | 0.017 | 0.024 | 0.023 | 0.02
24 |  |  |  | 0.021 | 0.021 | 0.021 | 0.02
25 |  |  |  | 0.022 | 0.025 |  | 0.03
26 |  |  |  | 0.019 | 0.024 | 0.024 | 0.02
27 |  |  |  | 0.03 | 0.027 | 0.03 | 0.03
28 |  |  |  | 0.024 | 0.026 | 0.027 | 0.03
29 |  |  |  | 0.028 | 0.046 |  | 0.05
30 |  |  |  | 0.019 | 0.022 |  | 0.02
31 |  |  |  | 0.021 | 0.024 | 0.021 | 0.02
Conventional or Direct Filtration
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | YES | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | Date: 4/10/2026
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | B
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2026-03-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.14 | 241 | 274.74 | 7.6 | 7.67 | 58.2953 | YES | 131
2 | 1.01 | 241 | 243.41 | 7.8 | 7.42 | 51.7958 | YES | 141
3 | 1.03 | 241 | 248.23 | 8.5 | 7.44 | 49.8936 | YES | 153
4 | 1.01 | 241 | 243.41 | 8.4 | 7.42 | 49.7577 | YES | 137
5 | 0.97 | 241 | 233.77 | 8.4 | 7.41 | 49.3548 | YES | 147
6 | 0.99 | 241 | 238.59 | 8.6 | 7.41 | 48.8122 | YES | 131
7 | 1.03 | 241 | 248.23 | 10.1 | 7.32 | 43.008 | YES | 125
8 | 0.97 | 241 | 233.77 | 10.4 | 7.4 | 43.0747 | YES | 122
9 | 1.02 | 241 | 245.82 | 8.6 | 7.36 | 48.1179 | YES | 139
10 | 1.09 | 241 | 262.69 | 7.7 | 7.36 | 51.5094 | YES | 137
11 | 1 | 241 | 241 | 8 | 7.4 | 50.6852 | YES | 139
12 | 1.09 | 241 | 262.69 | 8.1 | 7.35 | 49.9708 | YES | 125
13 | 1.18 | 241 | 284.38 | 8.3 | 7.35 | 49.8178 | YES | 141
14 | 1.13 | 241 | 272.33 | 7.9 | 7.32 | 50.3349 | YES | 127
15 | 1.17 | 241 | 281.97 | 8.1 | 7.27 | 49.015 | YES | 130
16 | 1.06 | 241 | 255.46 | 8.2 | 7.28 | 48.2532 | YES | 138
17 | 1.17 | 241 | 281.97 | 8.4 | 7.34 | 49.2543 | YES | 141
18 | 1.23 | 241 | 296.43 | 8.9 | 7.32 | 47.6287 | YES | 140
19 | 1.1 | 241 | 265.1 | 9.1 | 7.35 | 46.8044 | YES | 141
20 | 1.23 | 241 | 296.43 | 9.4 | 7.38 | 47.0614 | YES | 127
21 | 1.31 | 241 | 315.71 | 9.3 | 7.31 | 46.6383 | YES | 123
22 | 1.16 | 241 | 279.56 | 9 | 7.35 | 47.4391 | YES | 123
23 | 1.24 | 241 | 298.84 | 8.7 | 7.36 | 49.0132 | YES | 136
24 | 1.13 | 241 | 272.33 | 8.9 | 7.43 | 48.9631 | YES | 127
25 | 1.23 | 241 | 296.43 | 9 | 7.45 | 49.5474 | YES | 130
26 | 1.18 | 241 | 284.38 | 8.5 | 7.31 | 48.4637 | YES | 147
27 | 1.21 | 241 | 291.61 | 8.5 | 7.66 | 55.1045 | YES | 140
28 | 1.36 | 241 | 327.76 | 10.3 | 7.26 | 43.1365 | YES | 123
29 | 1.24 | 241 | 298.84 | 9.4 | 7.37 | 46.9485 | YES | 133
30 | 1.44 | 241 | 347.04 | 8.6 | 7.6 | 55.0085 | YES | 154
31 | 1.45 | 241 | 349.45 | 8.4 | 7.69 | 57.6575 | YES | 143
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2