## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Washington
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-08-01
System Name: | Banks Water Department |  |  | ID#: 41 | 00076 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.06 | 0.05 | 0.06
2 | 0.05 | 0.05 | 0.06 | 0.05 | 0.06 | 0.06 | 0.06
3 | 0.06 | 0.05 | 0.06 | 0.07 | 0.08 | 0.06 | 0.08
4 | 0.06 | 0.05 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07
5 | 0.06 | 0.06 | 0.06 | 0.07 | 0.06 | 0.06 | 0.07
6 | 0.07 | 0.05 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07
7 | 0.05 | 0.06 | 0.05 | 0.05 | 0.06 | 0.06 | 0.06
8 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
9 | 0.06 | 0.07 | 0.06 | 0.06 | 0.06 | 0.06 | 0.07
10 | 0.07 | 0.06 | 0.06 | 0.07 | 0.06 | 0.06 | 0.07
11 | 0.06 | 0.06 | 0.07 | 0.06 | 0.07 | 0.06 | 0.07
12 | 0.06 | 0.07 | 0.06 | 0.06 | 0.07 | 0.07 | 0.07
13 | 0.08 | 0.07 | 0.07 | 0.06 | 0.07 | 0.07 | 0.08
14 | 0.06 | 0.06 | 0.08 | 0.06 | 0.06 | 0.07 | 0.08
15 | 0.06 | 0.06 | 0.07 | 0.06 | 0.07 | 0.07 | 0.07
16 | 0.06 | 0.07 | 0.07 | 0.06 | 0.07 | 0.06 | 0.07
17 | 0.06 | 0.06 | 0.06 | 0.07 | 0.06 | 0.07 | 0.07
18 | 0.06 | 0.07 | 0.07 | 0.07 | 0.07 | 0.1 | 0.1
19 | 0.09 | 0.06 | 0.07 | 0.06 | 0.07 | 0.06 | 0.09
20 | 0.07 | 0.06 | 0.08 | 0.08 | 0.07 | 0.07 | 0.08
21 | 0.07 | 0.08 | 0.09 | 0.09 | 0.09 | 0.1 | 0.1
22 | 0.1 | 0.1 | 0.1 | 0.12 | 0.11 | 0.1 | 0.12
23 | 0.12 | 0.12 | 0.12 | 0.13 | 0.13 | 0.12 | 0.13
24 | 0.13 | 0.11 | 0.12 | 0.11 | 0.12 | 0.14 | 0.14
25 | 0.12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
26 | 0.12 | 0.13 | 0.13 | 0.14 | 0.09 | 0.07 | 0.14
27 | 0.07 | 0.07 | 0.07 | 0.07 | 0.08 | 0.09 | 0.09
28 | 0.07 | 0.08 | 0.07 | 0.07 | 0.12 | 0.09 | 0.12
29 | 0.06 | 0.06 | 0.06 | 0.07 | 0.09 | 0.09 | 0.09
30 | 0.06 | 0.07 | 0.07 | 0.07 | 0.11 | 0.1 | 0.11
31 | 0.07 | 0.07 | 0.07 | 0.2 | 0.25 | 0.2 | 0.25
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Jeffrey Olson
[5 empty] | SIGNATURE: Jeffrey Olson |  |  | 2022-09-02
[5 empty] | PHONE #: ( 503 ) - 729 -1028 |  |  | CERT #: 766039
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Banks Water Department |  | ID#: 41 | 00076 | Month/Year: | 2022-08-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.62 | 201 | 124.62 | 19.44 | 7.19 | 20.7674 | YES | 215
2 | 0.62 | 201 | 124.62 | 19.4444 | 7.24 | 21.1541 | YES | 215
3 | 0.6 | 201 | 120.6 | 18.8889 | 7.32 | 22.5774 | YES | 215
4 | 0.63 | 201 | 126.63 | 18.3333 | 7.27 | 23.0832 | YES | 215
5 | 0.69 | 201 | 138.69 | 17.7778 | 7.17 | 23.2432 | YES | 215
6 | 0.72 | 201 | 144.72 | 17.2222 | 7.12 | 23.7634 | YES | 215
7 | 0.73 | 201 | 146.73 | 17.7778 | 7.08 | 22.5777 | YES | 215
8 | 0.72 | 201 | 144.72 | 18.3333 | 7.14 | 22.2165 | YES | 215
9 | 0.76 | 201 | 152.76 | 18.3333 | 7.11 | 22.0698 | YES | 215
10 | 0.67 | 201 | 134.67 | 18.33 | 7.11 | 21.8472 | YES | 215
11 | 0.81 | 201 | 162.81 | 17.7778 | 7.14 | 23.3032 | YES | 215
12 | 0.79 | 201 | 158.79 | 17.7778 | 7.11 | 22.9905 | YES | 215
13 | 0.79 | 201 | 158.79 | 17.7778 | 7.13 | 23.163 | YES | 215
14 | 0.76 | 201 | 152.76 | 17.2222 | 7.11 | 23.7838 | YES | 215
15 | 0.75 | 201 | 150.75 | 17.2222 | 7.11 | 23.7565 | YES | 215
16 | 0.78 | 201 | 156.78 | 17.2222 | 7.08 | 23.5729 | YES | 215
17 | 0.78 | 201 | 156.78 | 17.7778 | 7.06 | 22.5387 | YES | 215
18 | 0.78 | 201 | 156.78 | 18.8889 | 7.07 | 20.99 | YES | 215
19 | 0.76 | 201 | 152.76 | 19.4444 | 7.06 | 20.0943 | YES | 215
20 | 0.72 | 201 | 144.72 | 19.4444 | 7.06 | 20.0017 | YES | 215
21 | 0.69 | 201 | 138.69 | 18.3333 | 7.06 | 21.4864 | YES | 215
22 | 0.68 | 201 | 136.68 | 18.3333 | 7.08 | 21.6231 | YES | 215
23 | 0.43 | 201 | 86.43 | 18.3333 | 7.08 | 21.009 | YES | 215
24 | 0.59 | 201 | 118.59 | 18.3333 | 7.13 | 21.8047 | YES | 215
25 | 0.67 | 201 | 134.67 | 18.3333 | 7.21 | 22.6752 | YES | 215
26 | 0.77 | 201 | 154.77 | 18.3333 | 7.2 | 22.8518 | YES | 215
27 | 0.86 | 201 | 172.86 | 18.3333 | 7.23 | 23.3498 | YES | 215
28 | 0.87 | 201 | 174.87 | 17.2222 | 7.27 | 25.5667 | YES | 215
29 | 0.88 | 201 | 176.88 | 17.2222 | 7.28 | 25.6916 | YES | 215
30 | 0.92 | 201 | 184.92 | 17.7778 | 7.28 | 24.8652 | YES | 215
31 | 0.92 | 201 | 184.92 | 18.3333 | 7.35 | 24.5883 | YES | 215
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2