## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Washington
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-09-01
System Name: | Banks Water Department |  |  | ID#: 41 | 00076 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.2 | 0.2 | 0.68 | 0.17 | 0.16 | 0.15 | 0.68
2 | 0.13 | 0.1 | 0.12 | 0.17 | 0.2 | 0.17 | 0.2
3 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15
4 | 0.14 | 0.15 | 0.14 | 0.14 | 0.14 | 0.1 | 0.15
5 | 0.13 | 0.13 | 0.14 | 0.14 | 0.16 | 0.14 | 0.16
6 | 0.13 | 0.14 | 0.13 | 0.15 | 0.15 | 0.14 | 0.15
7 | 0.14 | 0.14 | 0.15 | 0.13 | 0.14 | 0.15 | 0.15
8 | 0.15 | 0.14 | 0.13 | 0.13 | 0.15 | 0.14 | 0.15
9 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15 | 0.15
10 | 0.14 | 0.13 | 0.12 | 0.14 | 0.14 | 0.14 | 0.14
11 | 0.13 | 0.14 | 0.14 | 0.15 | 0.13 | 0.15 | 0.15
12 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | 0.14
13 | 0.13 | 0.13 | 0.15 | 0.14 | 0.15 | 0.13 | 0.15
14 | 0.14 | 0.13 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15
15 | 0.14 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.14
16 | 0.14 | 0.15 | 0.13 | 0.15 | 0.15 | 0.14 | 0.15
17 | 0.15 | 0.14 | 0.14 | 0.14 | 0.16 | 0.15 | 0.16
18 | 0.15 | 0.16 | 0.16 | 0.15 | 0.14 | 0.15 | 0.16
19 | 0.15 | 0.15 | 0.15 | 0.16 | 0.14 | 0.15 | 0.16
20 | 0.15 | 0.14 | 0.14 | 0.13 | 0.14 | 0.14 | 0.15
21 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.15
22 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15
23 | 0.15 | 0.15 | 0.15 | 0.15 | 0.16 | 0.15 | 0.16
24 | 0.14 | 0.15 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15
25 | 0.15 | 0.14 | 0.14 | 0.14 | 0.15 | 0.14 | 0.15
26 | 0.14 | 0.12 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14
27 | 0.14 | 0.13 | 0.14 | 0.15 | 0.13 | 0.14 | 0.15
28 | 0.15 | 0.13 | 0.14 | 0.15 | 0.13 | 0.14 | 0.15
29 | 0.13 | 0.13 | 0.14 | 0.15 | 0.15 | 0.14 | 0.14
30 | 0.14 | 0.14 | 0.13 | 0.15 | 0.14 | 0.13 | 0.15
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Jeffrey Olson
[5 empty] | SIGNATURE: Jeffrey Olson |  |  | 2022-10-04
[5 empty] | PHONE #: ( 503 ) - 729 -1028 |  |  | CERT #: 766039
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Banks Water Department |  | ID#: 41 | 00076 | Month/Year: | 2022-09-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.78 | 201 | 156.78 | 17.78 | 7.34 | 25.0191 | YES | 215
2 | 0.63 | 201 | 126.63 | 17.78 | 7.37 | 24.8692 | YES | 215
3 | 0.63 | 201 | 126.63 | 17.78 | 7.31 | 24.3188 | YES | 215
4 | 0.62 | 201 | 124.62 | 17.7778 | 7.33 | 24.4765 | YES | 215
5 | 0.64 | 201 | 128.64 | 17.7778 | 7.31 | 24.3504 | YES | 215
6 | 0.65 | 201 | 130.65 | 17.2222 | 7.29 | 25.1168 | YES | 215
7 | 0.65 | 201 | 130.65 | 17.2222 | 7.28 | 25.0234 | YES | 215
8 | 0.64 | 201 | 128.64 | 17.2222 | 7.29 | 25.0881 | YES | 215
9 | 0.63 | 201 | 126.63 | 16.6667 | 7.27 | 25.8178 | YES | 215
10 | 0.63 | 201 | 126.63 | 16.6667 | 7.23 | 25.436 | YES | 215
11 | 0.65 | 201 | 130.65 | 17.2222 | 7.26 | 24.8375 | YES | 215
12 | 0.65 | 201 | 130.65 | 17.7778 | 7.28 | 24.1069 | YES | 215
13 | 0.62 | 201 | 124.62 | 17.2222 | 7.27 | 24.8447 | YES | 215
14 | 0.62 | 201 | 124.62 | 17.2222 | 7.26 | 24.7522 | YES | 215
15 | 0.62 | 201 | 124.62 | 17.2222 | 7.25 | 24.6601 | YES | 215
16 | 0.62 | 201 | 124.62 | 17.2222 | 7.26 | 24.7522 | YES | 215
17 | 0.68 | 201 | 136.68 | 16.1111 | 7.19 | 26.1604 | YES | 215
18 | 0.7 | 201 | 140.7 | 16.1111 | 7.16 | 25.9291 | YES | 215
19 | 0.69 | 201 | 138.69 | 16.1111 | 7.15 | 25.8032 | YES | 215
20 | 0.69 | 201 | 138.69 | 16.1111 | 7.17 | 25.9961 | YES | 215
21 | 0.68 | 201 | 136.68 | 16.1111 | 7.17 | 25.9663 | YES | 215
22 | 0.74 | 201 | 148.74 | 16.1111 | 7.21 | 26.5374 | YES | 215
23 | 0.74 | 201 | 148.74 | 15.5556 | 7.23 | 27.7488 | YES | 215
24 | 0.74 | 201 | 148.74 | 15 | 7.23 | 28.7991 | YES | 215
25 | 0.75 | 201 | 150.75 | 15 | 7.21 | 28.6187 | YES | 215
26 | 0.74 | 201 | 148.74 | 15.5556 | 7.19 | 27.3392 | YES | 215
27 | 0.75 | 201 | 150.75 | 15.5556 | 7.21 | 27.5748 | YES | 215
28 | 0.74 | 201 | 148.74 | 15.5556 | 7.23 | 27.7488 | YES | 215
29 | 0.74 | 201 | 148.74 | 15.5556 | 7.23 | 27.7488 | YES | 215
30 | 0.67 | 201 | 134.67 | 15.5556 | 7.21 | 27.3238 | YES | 215
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2