## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Washington
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-10-01
System Name: | Banks Water Department |  |  | ID#: 41 | 00076 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | 0.14
2 | 0.13 | 0.14 | 0.14 | 0.13 | 0.13 | 0.12 | 0.14
3 | 0.13 | 0.14 | 0.13 | 0.14 | 0.01 | 0.01 | 0.14
4 | 0.01 | 0.01 | 0.01 | 0.01 | 0.06 | 0.08 | 0.08
5 | 0.07 | 0.07 | 0.08 | 0.07 | 0.08 | 0.07 | 0.08
6 | 0.07 | 0.07 | 0.08 | 0.06 | 0.09 | 0.08 | 0.09
7 | 0.06 | 0.06 | 0.08 | 0.07 | 0.06 | 0.08 | 0.08
8 | 0.07 | 0.06 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07
9 | 0.08 | 0.08 | 0.07 | 0.07 | 0.08 | 0.11 | 0.11
10 | 0.08 | 0.09 | 0.08 | 0.07 | 0.07 | 0.06 | 0.09
11 | 0.07 | 0.08 | 0.08 | 0.09 | 0.08 | 0.08 | 0.09
12 | 0.07 | 0.08 | 0.09 | 0.07 | 0.07 | 0.06 | 0.09
13 | 0.07 | 0.08 | 0.07 | 0.07 | 0.07 | 0.06 | 0.08
14 | 0.34 | 0.07 | 0.05 | 0.02 | 0.02 | 0.02 | 0.34
15 | 0.02 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03
16 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
17 | 0.02 | 0.02 | 0.02 | 0.04 | 0.03 | 0.03 | 0.04
18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
19 | 0.04 | 0.03 | 0.04 | 0.56 | 0.03 | 0.32 | 0.56
20 | 0.02 | 0.02 | 0.02 | 0.05 | 0.04 | 0.09 | 0.09
21 | 0.02 | *.02 | *.04 | *.04 | *.02 | 0.04 | 0.04
22 | 0.05 | 0.55 | 0.1 | 0.04 | 0.04 | 0.09 | 0.55
23 | 0.08 | 0.02 | 0.01 | 0.07 | 0.08 | 0.01 | 0.08
24 | 0.41 | 0.08 | 0.02 | 0.01 | 0.01 | 0.05 | 0.41
25 | 0.04 | 0.02 | 0.07 | 0.01 | 0.09 | 0.06 | 0.09
26 | 0.03 | 0.03 | 0.05 | 0.05 | 0.04 | 0.03 | 0.05
27 | 0.06 | 0.03 | 0.06 | 0.01 | 0.02 | 0.02 | 0.06
28 | 0.07 | 0.03 | 0.07 | 0.08 | 0.08 | 0.08 | 0.08
29 | 0.08 | 0.07 | 0.09 | 0.04 | 0.07 | 0.09 | 0.14
30 | 0.07 | 0.06 | 0.08 | 0.08 | 0.06 | 0.06 | 0.08
31 | 0.06 | 0.04 | 0.03 | 0.06 | 0.02 | 0.09 | 0.09
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: *Hand readings taken while new turbidity meters were being installed. |  |  |  |  | PRINTED NAME: Jeffrey Olson
[5 empty] | SIGNATURE: Jeffrey Olson |  |  | 2022-11-01
[5 empty] | PHONE #: ( 503 ) - 729 -1028 |  |  | CERT #: 766039
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Banks Water Department |  | ID#: 41 | 00076 | Month/Year: | 2022-10-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.63 | 201 | 126.63 | 15 | 7.17 | 27.8129 | YES | 215
2 | 0.58 | 201 | 116.58 | 15.5556 | 7.17 | 26.6446 | YES | 215
3 | 0.62 | 201 | 124.62 | 15 | 7.17 | 27.7811 | YES | 215
4 | 0.7 | 201 | 140.7 | 15 | 7.22 | 28.5617 | YES | 215
5 | 0.74 | 201 | 148.74 | 15 | 7.14 | 27.8524 | YES | 215
6 | 0.77 | 201 | 154.77 | 14.4444 | 7.15 | 29.1136 | YES | 215
7 | 0.78 | 201 | 156.78 | 15 | 7.1 | 27.5671 | YES | 215
8 | 0.78 | 201 | 156.78 | 15 | 7.1 | 27.5671 | YES | 215
9 | 0.77 | 201 | 154.77 | 15 | 7.1 | 27.5356 | YES | 215
10 | 0.76 | 201 | 152.76 | 15 | 7.12 | 27.7094 | YES | 215
11 | 0.75 | 201 | 150.75 | 14.4444 | 7.13 | 28.8323 | YES | 215
12 | 0.75 | 201 | 150.75 | 13.8889 | 7.13 | 29.9226 | YES | 215
13 | 0.75 | 201 | 150.75 | 14.4444 | 7.12 | 28.7255 | YES | 215
14 | 0.8 | 201 | 160.8 | 14.4444 | 7.16 | 29.322 | YES | 215
15 | 0.83 | 201 | 166.83 | 14.4444 | 7.13 | 29.0968 | YES | 215
16 | 0.82 | 201 | 164.82 | 15 | 7.13 | 28.0039 | YES | 215
17 | 0.82 | 201 | 164.82 | 15 | 7.21 | 28.8483 | YES | 215
18 | 0.84 | 201 | 168.84 | 13.8889 | 7.17 | 30.6828 | YES | 215
19 | 0.83 | 201 | 166.83 | 13.8889 | 7.23 | 31.3368 | YES | 215
20 | 0.81 | 201 | 162.81 | 13.8889 | 7.21 | 31.0347 | YES | 215
21 | 0.79 | 201 | 158.79 | 13.3333 | 7.22 | 32.2518 | YES | 215
22 | 0.77 | 201 | 154.77 | 12.2222 | 7.16 | 34.4423 | YES | 215
23 | 0.74 | 201 | 148.74 | 11.6667 | 7.13 | 35.2111 | YES | 215
24 | 0.72 | 201 | 144.72 | 11.6667 | 7.12 | 35.0138 | YES | 215
25 | 0.72 | 201 | 144.72 | 11.1111 | 7.09 | 35.9158 | YES | 215
26 | 0.73 | 201 | 146.73 | 10.5556 | 7.06 | 36.8849 | YES | 215
27 | 0.71 | 201 | 142.71 | 10.5556 | 7.06 | 36.8034 | YES | 215
28 | 0.78 | 201 | 156.78 | 10.5556 | 7.04 | 36.835 | YES | 215
29 | 0.83 | 201 | 166.83 | 11.1111 | 7.02 | 35.4916 | YES | 215
30 | 0.95 | 201 | 190.95 | 11.1111 | 7.02 | 35.964 | YES | 215
31 | 1 | 201 | 201 | 11.6667 | 7.01 | 34.775 | YES | 215
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2