## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Washington
Conventional or Direct Filtration | [6 empty] | Month/Year: | November/2022
System Name: | Banks Water Department |  |  | ID#: 41 | 00076 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.03 | 0.02 | 0.08 | 0.02 | 0.08
2 | 0.04 | 0.03 | 0.07 | 0.08 | 0.02 | 0.06 | 0.08
3 | 0.09 | 0.02 | 0.03 | 0.07 | 0.02 | 0.03 | 0.09
4 | 0.02 | 0.02 | 0.08 | 0.07 | 0.07 | 0.04 | 0.08
5 | 0.04 | 0.06 | 0.1 | 0.09 | 0.07 | 0.04 | 0.1
6 | 0.05 | 0.09 | 0.08 | 0.09 | 0.04 | 0.02 | 0.09
7 | 0.09 | 0.08 | 0.03 | 0.09 | 0.04 | 0.01 | 0.09
8 | 0.09 | 0.06 | 0.04 | 0.07 | 0.05 | 0.04 | 0.09
9 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.09 | 0.09
10 | 0.13 | 0.21 | 0.18 | 0.2 | 0.2 | 0.14 | 0.21
11 | 0.11 | 0.15 | 0.09 | 0.17 | 0.17 | 0.1 | 0.17
12 | 0.1 | 0.17 | 0.13 | 0.15 | 0.16 | 0.13 | 0.17
13 | 0.17 | 0.1 | 0.12 | 0.16 | 0.12 | 0.17 | 0.17
14 | 0.09 | 0.17 | 0.12 | 0.08 | 0.17 | 0.16 | 0.17
15 | 0.16 | 0.11 | 0.12 | 0.17 | 0.11 | 0.1 | 0.17
16 | 0.1 | 0.12 | 0.1 | 0.08 | 0.11 | 0.04 | 0.12
17 | 0.11 | 0.04 | 0.11 | 0.03 | 0.02 | 0.02 | 0.11
18 | 0.06 | 0.03 | 0.06 | 0.02 | 0.02 | 0.06 | 0.06
19 | 0.01 | 0.03 | 0.08 | 0.07 | 0.09 | 0.09 | 0.09
20 | 0.09 | 0.07 | 0.07 | 0.06 | 0.08 | 0.12 | 0.12
21 | 0.07 | 0.09 | 0.1 | 0.04 | 0.06 | 0.02 | 0.1
22 | 0.01 | 0.05 | 0.05 | 0.05 | 0.03 | 0.04 | 0.05
23 | 0.04 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06 | 0.06
24 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.05 | 0.05
26 | 0.05 | 0.04 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
27 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
28 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06 | 0.06 | 0.06
29 | 0.06 | 0.05 | 0.06 | 0.05 | 0.06 | 0.06 | 0.06
30 | 0.06 | 0.06 | 0.1 | 0.39 | 1.24 | 2.24 | 2.24
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Jeffrey Olson
[5 empty] | SIGNATURE: Jeffrey Olson |  |  | 2022-12-12
[5 empty] | PHONE #: ( 503 ) - 729 -1028 |  |  | CERT #: 766039
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.86 | 201 | 172.86 | 11.06 | 7.04 | 35.9722 | YES | 215
2 | 0.84 | 201 | 168.84 | 11 | 7.02 | 35.7856 | YES | 215
3 | 0.76 | 201 | 152.76 | 10.11 | 7 | 37.31 | YES | 215
4 | 0.75 | 201 | 150.75 | 9.78 | 7 | 38.074 | YES | 215
5 | 0.71 | 201 | 142.71 | 10 | 7 | 37.3689 | YES | 215
6 | 0.59 | 201 | 118.59 | 9.61 | 6.91 | 36.6629 | YES | 215
7 | 0.57 | 201 | 114.57 | 9.06 | 6.91 | 37.907 | YES | 215
8 | 0.57 | 201 | 114.57 | 8.22 | 6.85 | 39.2103 | YES | 215
9 | 0.59 | 201 | 118.59 | 7.06 | 6.83 | 42.1003 | YES | 215
10 | 0.61 | 201 | 122.61 | 7.33 | 6.83 | 41.4543 | YES | 215
11 | 0.72 | 201 | 144.72 | 7.44 | 6.91 | 42.8509 | YES | 215
12 | 0.75 | 201 | 150.75 | 7.67 | 6.98 | 43.4027 | YES | 215
13 | 0.76 | 201 | 152.76 | 7.33 | 6.94 | 43.8165 | YES | 215
14 | 0.74 | 201 | 148.74 | 7.33 | 6.95 | 43.8715 | YES | 215
15 | 0.73 | 201 | 146.73 | 7.28 | 7 | 44.7471 | YES | 215
16 | 0.73 | 201 | 146.73 | 6.89 | 7.01 | 46.0794 | YES | 215
17 | 0.71 | 201 | 142.71 | 6.56 | 7 | 46.8266 | YES | 215
18 | 0.75 | 201 | 150.75 | 5.89 | 6.97 | 48.664 | YES | 215
19 | 0.8 | 201 | 160.8 | 5.89 | 7 | 49.4673 | YES | 215
20 | 0.79 | 201 | 158.79 | 5.44 | 7.02 | 51.284 | YES | 215
21 | 0.79 | 201 | 158.79 | 5.67 | 7.12 | 52.3357 | YES | 215
22 | 0.78 | 201 | 156.78 | 6.11 | 7.06 | 49.684 | YES | 215
23 | 0.91 | 201 | 182.91 | 6.44 | 7.06 | 49.3291 | YES | 215
24 | 0.84 | 201 | 168.84 | 6.94 | 7.06 | 47.3342 | YES | 215
25 | 0.83 | 201 | 166.83 | 6.61 | 7.04 | 47.9882 | YES | 215
26 | 0.83 | 201 | 166.83 | 6.94 | 7.06 | 47.2804 | YES | 215
27 | 0.83 | 201 | 166.83 | 7.11 | 7.04 | 46.4201 | YES | 215
28 | 0.77 | 201 | 154.77 | 6.89 | 7.04 | 46.7827 | YES | 215
29 | 0.76 | 201 | 152.76 | 6.67 | 7.01 | 46.9165 | YES | 215
30 | 0.67 | 201 | 134.67 | 6.61 | 7.07 | 47.6252 | YES | 215
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2