## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-09-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2024-09-01 |  |  |  | 0.03 | 0.03 |  | 0.03
2024-09-02 |  | 0.031 | 0.03 | 0.031 | 0.03 |  | 0.031
2024-09-03 |  | 0.031 | 0.03 | 0.03 |  |  | 0.031
2024-09-04 |  |  | 0.03 | 0.03 |  |  | 0.03
2024-09-05 |  |  | 0.032 | 0.031 |  |  | 0.032
2024-09-06 |  |  | 0.03 | 0.065 |  |  | 0.065
2024-09-07 |  |  | 0.032 | 0.03 |  |  | 0.032
2024-09-08 |  |  |  | 0.03 | 0.03 | 0.03 | 0.03
2024-09-09 |  |  | 0.047 | 0.029 | 0.032 |  | 0.047
2024-09-10 |  |  | 0.03 | 0.031 |  |  | 0.031
2024-09-11 |  |  | 0.033 |  |  |  | 0.033
2024-09-12 |  |  | 0.061 |  |  |  | 0.061
2024-09-13 |  |  | 0.098 | 0.032 |  |  | 0.098
2024-09-14 |  |  |  | 0.032 | 0.034 | 0.037 | 0.037
2024-09-15 |  |  | 0.03 |  |  |  | 0.03
2024-09-16 |  |  | 0.027 |  |  |  | 0.027
2024-09-17 |  |  | 0.036 | 0.032 |  |  | 0.036
2024-09-18 |  |  | 0.031 | 0.05 |  |  | 0.05
2024-09-19 |  |  | 0.04 | 0.04 |  |  | 0.04
2024-09-20 |  |  | 0.043 | 0.05 |  |  | 0.05
2024-09-21 |  |  | 0.065 |  |  |  | 0.065
2024-09-22 |  |  | 0.034 |  |  |  | 0.034
2024-09-23 |  |  | 0.032 |  |  |  | 0.032
2024-09-24 |  |  | 0.04 |  |  |  | 0.04
2024-09-25 |  |  | 0.041 |  |  |  | 0.041
2024-09-26 |  |  | 0.047 | 0.045 | 0.043 |  | 0.047
2024-09-27 |  |  | 0.08 |  |  |  | 0.08
2024-09-28 |  |  | 0.034 |  |  |  | 0.034
2024-09-29 |  |  | 0.05 | 0.06 |  |  | 0.06
2024-09-30 |  |  |  | 0.053 | 0.043 |  | 0.053
2024-10-01 | [6 empty] | Off
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE:
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 66 | 46.2 | 16.7 | 7.8 | 31.615 | Yes | 68.1
2 | 0.77 | 66 | 50.82 | 16.7 | 7.9 | 33.0695 | Yes | 68.9
3 | 0.83 | 66 | 54.78 | 16.3 | 7.6 | 30.6009 | Yes | 67.3
4 | 0.8 | 66 | 52.8 | 18 | 7.8 | 29.3198 | Yes | 63.2
5 | 0.8 | 66 | 52.8 | 17.6 | 7.8 | 30.1137 | Yes | 66.8
6 | 0.9 | 66 | 59.4 | 17.8 | 7.5 | 26.8863 | Yes | 66.8
7 | 0.8 | 66 | 52.8 | 17.5 | 7.5 | 27.12 | Yes | 68.1
8 | 0.74 | 66 | 48.84 | 18.3 | 7.7 | 27.5008 | Yes | 67.2
9 | 0.9 | 66 | 59.4 | 18.4 | 7.3 | 23.9709 | Yes | 61.7
10 | 0.8 | 66 | 52.8 | 18 | 7.3 | 24.343 | Yes | 68.6
11 | 0.9 | 66 | 59.4 | 17.2 | 7.4 | 26.9667 | Yes | 68.6
12 | 0.9 | 66 | 59.4 | 17.3 | 7.4 | 26.7867 | Yes | 65.6
13 | 0.9 | 66 | 59.4 | 16.9 | 7.7 | 30.7543 | Yes | 64.3
14 | 0.78 | 66 | 51.48 | 16.8 | 8.5 | 41.0384 | Yes | 66
15 | 0.76 | 66 | 50.16 | 16.1 | 8.5 | 42.8897 | Yes | 66
16 | 0.7 | 66 | 46.2 | 16.5 | 8 | 34.4993 | Yes | 65
17 | 0.9 | 66 | 59.4 | 15.7 | 8.5 | 44.7434 | Yes | 63.1
18 | 0.8 | 66 | 52.8 | 17 | 7.3 | 26.0326 | Yes | 63.7
19 | 0.9 | 66 | 59.4 | 16 | 7.2 | 27.1283 | Yes | 63.9
20 | 0.89 | 66 | 58.74 | 15.2 | 7.2 | 28.5872 | Yes | 61
21 | 1 | 66 | 66 | 15.3 | 7.3 | 29.8427 | Yes | 63.8
22 | 0.9 | 66 | 59.4 | 15.8 | 7.5 | 30.7322 | Yes | 64
23 | 0.95 | 66 | 62.7 | 15.7 | 7.3 | 28.8905 | Yes | 63.7
24 | 0.8 | 66 | 52.8 | 16.4 | 7.2 | 26.1106 | Yes | 64
25 | 0.86 | 66 | 56.76 | 16.5 | 7.4 | 28.1312 | Yes | 63.7
26 | 0.95 | 66 | 62.7 | 16.1 | 7.1 | 26.1119 | Yes | 64
27 | 0.75 | 66 | 49.5 | 16.4 | 7.5 | 29.0245 | Yes | 63
28 | 0.79 | 66 | 52.14 | 15.7 | 6.9 | 24.4435 | Yes | 64.2
29 | 0.8 | 66 | 52.8 | 14.5 | 7.5 | 33.1349 | Yes | 63
30 | 0.73 | 66 | 48.18 | 14.4 | 7.5 | 33.0918 | Yes | 62.7
31 | off | 66 | Off |  |  | Off | Off
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@dhsoha.state.or.us 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
Page 2 Of 2