## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2024-11-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2024-11-01 |  |  |  |  | 0.03 | 0.03 | 0.03
2024-11-02 |  |  | 0.03 | 0.04 |  |  | 0.04
2024-11-03 | [6 empty] | Off
2024-11-04 | [6 empty] | Off
2024-11-05 |  |  | 0.05 | 0.04 |  |  | 0.05
2024-11-06 |  |  |  | 0.05 | 0.04 |  | 0.05
2024-11-07 | [6 empty] | Off
2024-11-08 | [6 empty] | Off
2024-11-09 |  |  |  |  | 0.08 | 0.07 | 0.08
2024-11-10 | 0.07 | 0.09 | 0.09 | 0.08 | 0.07 | 0.07 | 0.09
2024-11-11 | 0.09 | 0.2 | 0.04 | 0.04 | 0.04 | 0.04 | 0.2
2024-11-12 |  |  |  |  | 0.04 | 0.05 | 0.05
2024-11-13 | [6 empty] | Off
2024-11-14 | [6 empty] | Off
2024-11-15 | [6 empty] | Off
2024-11-16 | [6 empty] | Off
2024-11-17 | [6 empty] | Off
2024-11-18 | [6 empty] | Off
2024-11-19 | [6 empty] | Off
2024-11-20 | [6 empty] | Off
2024-11-21 |  |  | 0.08 | 0.09 |  | 0.05 | 0.09
2024-11-22 |  |  |  | 0.05 |  | 0.08 | 0.08
2024-11-23 |  |  | 0.09 | 0.17 |  |  | 0.17
2024-11-24 |  |  | 0.08 |  |  |  | 0.08
2024-11-25 |  |  | 0.04 | 0.05 | 0.04 |  | 0.05
2024-11-26 |  |  | 0.04 | 0.04 | 0.04 |  | 0.04
2024-11-27 |  |  | 0.04 | 0.04 | 0.04 |  | 0.04
2024-11-28 |  |  | 0.08 | 0.08 | 0.04 |  | 0.08
2024-11-29 |  |  | 0.04 | 0.04 |  | 0.04 | 0.04
2024-11-30 | 0.03 |  | 0.04 |  |  | 0.03 | 0.04
2024-12-01 | [6 empty] | Off
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: WTP-A experienced more downtime than usual this month due to intake pump failure. WTP-B was used in it's place. |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE: 12/5/2024
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2024-11-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 66 | 72.6 | 13.9 | 6.7 | 26.5257 | Yes
2 | 1.02 | 66 | 67.32 | 14.3 | 6.9 | 27.5654 | Yes
3 | off | 66 | Off |  |  | Off | Off
4 | off | 66 | Off |  |  | Off | Off
5 | 0.77 | 66 | 50.82 | 13.2 | 7.7 | 38.7625 | Yes
6 | 0.88 | 66 | 58.08 | 12.7 | 7.9 | 43.671 | Yes
7 | off | 66 | Off |  |  | Off | Off
8 | off | 66 | Off |  |  | Off | Off
9 | 0.77 | 66 | 50.82 | 12.5 | 6.4 | 25.0902 | Yes
10 | 0.7 | 66 | 46.2 | 13 | 6.5 | 24.9824 | Yes
11 | 0.75 | 66 | 49.5 | 11.7 | 7.7 | 42.854 | Yes
12 | 0.96 | 66 | 63.36 | 12.8 | 6.8 | 29.1623 | Yes
13 | off | 66 | Off |  |  | Off | Off
14 | off | 66 | Off |  |  | Off | Off
15 | off | 66 | Off |  |  | Off | Off
16 | off | 66 | Off |  |  | Off | Off
17 | off | 66 | Off |  |  | Off | Off
18 | off | 66 | Off |  |  | Off | Off
19 | off | 66 | Off |  |  | Off | Off
20 | off | 66 | Off |  |  | Off | Off
21 | 0.93 | 66 | 61.38 | 13.4 | 6.5 | 24.9703 | Yes
22 | 1.05 | 66 | 69.3 | 13.5 | 6.8 | 28.1165 | Yes
23 | 1.06 | 66 | 69.96 | 12.8 | 6.9 | 30.6113 | Yes
24 | 0.97 | 66 | 64.02 | 13.3 | 6.8 | 28.2359 | Yes
25 | 0.88 | 66 | 58.08 | 14.7 | 7.1 | 28.4491 | Yes
26 | 1 | 66 | 66 | 13 | 6.6 | 26.8365 | Yes
27 | 0.9 | 66 | 59.4 | 12.8 | 6.7 | 27.9075 | Yes
28 | 1 | 66 | 66 | 12 | 6.9 | 32.7926 | Yes
29 | 0.9 | 66 | 59.4 | 11.5 | 7 | 34.6463 | Yes
30 | 1.1 | 66 | 72.6 | 11 | 7.3 | 40.5779 | Yes
31 | off | 66 | Off |  |  | Off | Off
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@dhsoha.state.or.us 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
Page 2 Of 2