## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-02-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-02-01 |  |  |  |  | 0.14 |  | 0.14
2025-02-02 |  |  |  |  | 0.04 | 0.04 | 0.04
2025-02-03 |  |  |  | 0.04 |  |  | 0.04
2025-02-04 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-02-05 |  |  |  | 0.03 | 0.03 |  | 0.03
2025-02-06 |  |  |  | 0.03 |  |  | 0.03
2025-02-07 |  |  | 0.04 | 0.04 |  |  | 0.04
2025-02-08 |  |  |  | 0.05 | 0.04 |  | 0.05
2025-02-09 |  |  |  |  | 0.04 |  | 0.04
2025-02-10 |  |  |  | 0.04 |  |  | 0.04
2025-02-11 |  |  |  | 0.03 |  |  | 0.03
2025-02-12 |  |  |  | 0.04 | 0.05 |  | 0.05
2025-02-13 |  |  |  | 0.06 |  |  | 0.06
2025-02-14 |  |  |  |  | 0.04 | 0.04 | 0.04
2025-02-15 | [5 empty] | 0.04 | 0.04
2025-02-16 |  |  |  | 0.06 |  |  | 0.06
2025-02-17 |  |  |  | 0.04 |  |  | 0.04
2025-02-18 |  |  |  | 0.05 | 0.2 |  | 0.2
2025-02-19 |  |  |  | 0.08 | 0.05 |  | 0.08
2025-02-20 |  |  |  | 0.09 | 0.04 |  | 0.09
2025-02-21 |  |  | 0.04 | 0.04 |  |  | 0.04
2025-02-22 |  |  |  |  | 0.05 | 0.06 | 0.06
2025-02-23 | [6 empty] | Off
2025-02-24 | [6 empty] | Off
2025-02-25 | [6 empty] | Off
2025-02-26 |  |  |  | 0.08 | 0.07 |  | 0.08
2025-02-27 |  |  |  | 0.08 |  |  | 0.08
2025-02-28 |  |  |  | 0.08 | 0.06 |  | 0.08
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE: 3/4/2025
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-02-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.9 | 66 | 59.4 | 8.8 | 6.7 | 37.1921 | Yes | 70
2 | 0.9 | 66 | 59.4 | 10.2 | 6.2 | 28.7317 | Yes | 70
3 | 0.9 | 66 | 59.4 | 8.9 | 6.4 | 33.349 | Yes | 70
4 | 1 | 66 | 66 | 9.3 | 6.4 | 32.8669 | Yes | 70
5 | 0.9 | 66 | 59.4 | 9.5 | 6.4 | 32.1015 | Yes | 70
6 | 1.1 | 66 | 72.6 | 7.5 | 7.2 | 49.3666 | Yes | 70
7 | 1.1 | 66 | 72.6 | 7.3 | 6.9 | 44.9864 | Yes | 70
8 | 1.1 | 66 | 72.6 | 8.8 | 6.7 | 38.0264 | Yes | 70
9 | 1 | 66 | 66 | 8.9 | 7 | 41.4643 | Yes | 70
10 | 1 | 66 | 66 | 8.1 | 6.9 | 42.1974 | Yes | 70
11 | 0.9 | 66 | 59.4 | 7.6 | 7.1 | 46.2651 | Yes | 70
12 | 1 | 66 | 66 | 8.4 | 6.6 | 37.2845 | Yes | 70
13 | 1.1 | 66 | 72.6 | 8.1 | 7.5 | 52.7793 | Yes | 70
14 | 1.1 | 66 | 72.6 | 8.4 | 6.7 | 39.0275 | Yes | 70
15 | 0.91 | 66 | 60.06 | 8.4 | 7.5 | 50.6132 | Yes | 70
16 | 0.99 | 66 | 65.34 | 9.3 | 7.1 | 41.7802 | Yes | 70
17 | 1 | 66 | 66 | 9.6 | 6.5 | 33.3578 | Yes | 70
18 | 0.9 | 66 | 59.4 | 10.5 | 6.5 | 31.1674 | Yes | 70
19 | 1 | 66 | 66 | 10.4 | 6.4 | 30.6579 | Yes | 70
20 | 1 | 66 | 66 | 11.1 | 6.7 | 32.4491 | Yes | 70
21 | 1.1 | 66 | 72.6 | 10.4 | 6.5 | 32.0514 | Yes | 70
22 | 1.1 | 66 | 72.6 | 11.1 | 6.4 | 29.6575 | Yes | 70
23 | off | 66 | Off |  |  | Off | Off | 70
24 | off | 66 | Off |  |  | Off | Off | 70
25 | off | 66 | Off |  |  | Off | Off | 70
26 | 1 | 66 | 66 | 13 | 6.5 | 25.856 | Yes | 70
27 | 0.84 | 66 | 55.44 | 11.6 | 6.2 | 26.1869 | Yes | 70
28 | 1.1 | 66 | 72.6 | 11.4 | 6.5 | 30.0933 | Yes | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2