## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-03-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-03-01 |  |  |  |  | 0.05 |  | 0.05
2025-03-02 |  |  |  | 0.05 | 0.04 |  | 0.05
2025-03-03 |  |  |  |  | 0.04 |  | 0.04
2025-03-04 |  |  |  | 0.04 |  |  | 0.04
2025-03-05 |  |  |  | 0.05 | 0.04 |  | 0.05
2025-03-06 |  |  |  |  | 0.04 |  | 0.04
2025-03-07 |  |  |  |  | 0.05 |  | 0.05
2025-03-08 |  |  |  |  | 0.04 |  | 0.04
2025-03-09 |  |  | 0.05 |  |  |  | 0.05
2025-03-10 |  |  |  |  | 0.08 | 0.07 | 0.08
2025-03-11 |  |  |  |  | 0.05 |  | 0.05
2025-03-12 |  |  |  |  | 0.04 | 0.04 | 0.04
2025-03-13 |  |  |  | 0.06 |  |  | 0.06
2025-03-14 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-03-15 |  |  |  |  | 0.06 |  | 0.06
2025-03-16 |  |  |  |  | 0.05 |  | 0.05
2025-03-17 |  |  |  |  | 0.05 | 0.05 | 0.05
2025-03-18 |  |  |  | 0.04 |  |  | 0.04
2025-03-19 |  |  |  |  | 0.04 | 0.04 | 0.04
2025-03-20 |  |  |  | 0.04 |  |  | 0.04
2025-03-21 |  |  | 0.04 | 0.22 |  |  | 0.22
2025-03-22 | [6 empty] | Off
2025-03-23 |  |  |  | 0.05 |  |  | 0.05
2025-03-24 |  |  |  |  | 0.05 | 0.05 | 0.05
2025-03-25 |  |  |  | 0.05 | 0.05 | 0.05 | 0.05
2025-03-26 |  |  |  |  | 0.06 | 0.05 | 0.06
2025-03-27 |  |  |  | 0.05 |  |  | 0.05
2025-03-28 |  |  |  | 0.06 |  |  | 0.06
2025-03-29 |  |  |  | 0.12 | 0.05 |  | 0.12
2025-03-30 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-03-31 |  |  |  | 0.04 |  |  | 0.04
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE:
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 66 | 72.6 | 11.1 | 6.6 | 31.7141 | Yes | 70
2 | 1 | 66 | 66 | 11.3 | 6.6 | 30.9795 | Yes | 70
3 | 1 | 66 | 66 | 11.7 | 6.5 | 29.219 | Yes | 70
4 | 1 | 66 | 66 | 11.9 | 6.4 | 27.9177 | Yes | 70
5 | 1.1 | 66 | 72.6 | 12.5 | 7 | 32.556 | Yes | 70
6 | 1.1 | 66 | 72.6 | 10.4 | 6.8 | 35.4942 | Yes | 70
7 | 1.4 | 66 | 92.4 | 11.3 | 6.4 | 30.2463 | Yes | 70
8 | 1.4 | 66 | 92.4 | 11.4 | 6.5 | 31.0813 | Yes | 70
9 | 1.3 | 66 | 85.8 | 10.4 | 6.8 | 36.2854 | Yes | 70
10 | 1.2 | 66 | 79.2 | 10.5 | 6.6 | 33.3054 | Yes | 70
11 | 1 | 66 | 66 | 10.2 | 7 | 38.094 | Yes | 70
12 | 0.9 | 66 | 59.4 | 10.2 | 7.3 | 41.8121 | Yes | 70
13 | 1 | 66 | 66 | 10 | 7.4 | 44.3757 | Yes | 70
14 | 0.9 | 66 | 59.4 | 9.3 | 7.5 | 47.6101 | Yes | 70
15 | 1.1 | 66 | 72.6 | 9.8 | 7.1 | 40.9358 | Yes | 70
16 | 1.2 | 66 | 79.2 | 10.6 | 6.7 | 34.2386 | Yes | 70
17 | 0.9 | 66 | 59.4 | 11.7 | 6.5 | 28.9087 | Yes | 70
18 | 1.1 | 66 | 72.6 | 10.9 | 6.5 | 31.0545 | Yes | 70
19 | 1 | 66 | 66 | 10.4 | 6.9 | 36.3303 | Yes | 70
20 | 1.1 | 66 | 72.6 | 10.6 | 6.7 | 33.8659 | Yes | 70
21 | 1 | 66 | 66 | 12 | 6.8 | 31.7031 | Yes | 70
22 | off | 66 | Off |  |  | Off | Off
23 | 1.1 | 66 | 72.6 | 11.4 | 6.5 | 30.0933 | Yes | 70
24 | 1.1 | 66 | 72.6 | 11.8 | 6.4 | 28.3912 | Yes | 70
25 | 1 | 66 | 66 | 11.9 | 6.2 | 26.1453 | Yes | 70
26 | 1.2 | 66 | 79.2 | 11.9 | 6.5 | 29.4802 | Yes | 70
27 | 1.3 | 66 | 85.8 | 11 | 6.3 | 29.4903 | Yes | 70
28 | 1.3 | 66 | 85.8 | 10.9 | 6.4 | 30.6843 | Yes | 70
29 | 1.2 | 66 | 79.2 | 10.5 | 6.7 | 34.4584 | Yes | 70
30 | 1.2 | 66 | 79.2 | 10.2 | 6.4 | 31.7251 | Yes | 70
31 | 1.4 | 66 | 92.4 | 9.5 | 6.7 | 37.5699 | Yes | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2