## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-04-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-04-01 |  |  |  | 0.05 | 0.04 |  | 0.05
2025-04-02 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-04-03 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-04-04 |  |  |  |  | 0.05 | 0.05 | 0.05
2025-04-05 |  |  |  |  | 0.04 | 0.04 | 0.04
2025-04-06 |  |  |  |  | 0.04 |  | 0.04
2025-04-07 |  |  |  | 0.07 |  |  | 0.07
2025-04-08 |  |  |  | 0.05 | 0.14 |  | 0.14
2025-04-09 |  |  |  | 0.04 |  |  | 0.04
2025-04-10 |  |  |  |  | 0.04 |  | 0.04
2025-04-11 |  |  |  |  | 0.05 |  | 0.05
2025-04-12 |  |  |  | 0.04 |  |  | 0.04
2025-04-13 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-04-14 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-04-15 |  |  |  | 0.04 | 0.04 | 0.04 | 0.04
2025-04-16 |  |  |  | 0.04 |  |  | 0.04
2025-04-17 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-04-18 |  |  |  |  | 0.04 | 0.04 | 0.04
2025-04-19 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-04-20 |  |  |  | 0.05 |  |  | 0.05
2025-04-21 |  |  | 0.04 | 0.05 |  |  | 0.05
2025-04-22 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-04-23 |  |  |  |  | 0.05 | 0.04 | 0.05
2025-04-24 |  |  |  | 0.04 |  |  | 0.04
2025-04-25 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-04-26 |  |  |  |  | 0.05 | 0.05 | 0.05
2025-04-27 |  |  |  | 0.05 |  |  | 0.05
2025-04-28 |  |  |  | 0.04 | 0.05 | 0.05 | 0.05
2025-04-29 |  |  |  | 0.05 | 0.06 |  | 0.06
2025-04-30 |  |  |  | 0.05 | 0.06 |  | 0.06
2025-05-01 | [6 empty] | Off
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE:
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
2025-04-01 | 1.3 | 66 | 85.8 | 9.8 | 6.5 | 34.0323 | Yes | 70
2025-04-02 | 1.3 | 66 | 85.8 | 10 | 6.7 | 35.9761 | Yes | 70
2025-04-03 | 1.3 | 66 | 85.8 | 10.1 | 6.7 | 35.7452 | Yes | 70
2025-04-04 | 1.3 | 66 | 85.8 | 10.8 | 6.8 | 35.3632 | Yes | 70
2025-04-05 | 1.3 | 66 | 85.8 | 11.6 | 7 | 35.9729 | Yes | 70
2025-04-06 | 1.3 | 66 | 85.8 | 10.7 | 6.9 | 36.8349 | Yes | 70
2025-04-07 | 1.3 | 66 | 85.8 | 10.5 | 6.8 | 36.0523 | Yes | 70
2025-04-08 | 1.1 | 66 | 72.6 | 10.4 | 6.8 | 35.4942 | Yes | 70
2025-04-09 | 1.1 | 66 | 72.6 | 9.7 | 6.8 | 37.1329 | Yes | 70
2025-04-10 | 1 | 66 | 66 | 10.7 | 6.9 | 35.6351 | Yes | 70
2025-04-11 | 1.1 | 66 | 72.6 | 10.7 | 6.9 | 36.0301 | Yes | 70
2025-04-12 | 1.2 | 66 | 79.2 | 10 | 6.9 | 38.1177 | Yes | 70
2025-04-13 | 1.1 | 66 | 72.6 | 10.7 | 7.1 | 38.6022 | Yes | 70
2025-04-14 | 1.8 | 66 | 118.8 | 12.3 | 7.2 | 38.9337 | Yes | 70
2025-04-15 | 1.9 | 66 | 125.4 | 10.6 | 7.1 | 42.4946 | Yes | 70
2025-04-16 | 1.4 | 66 | 92.4 | 10.7 | 6.6 | 33.6093 | Yes | 70
2025-04-17 | 1 | 66 | 66 | 12.1 | 7.5 | 40.0369 | Yes | 70
2025-04-18 | 0.9 | 66 | 59.4 | 12 | 7.7 | 42.7325 | Yes | 70
2025-04-19 | 1.4 | 66 | 92.4 | 12 | 7.2 | 37.9723 | Yes | 70
2025-04-20 | 1.1 | 66 | 72.6 | 10.8 | 7.5 | 44.0957 | Yes | 70
2025-04-21 | 1.4 | 66 | 92.4 | 10.5 | 7.4 | 44.9212 | Yes | 70
2025-04-22 | 1.1 | 66 | 72.6 | 11.9 | 7.4 | 39.6169 | Yes | 70
2025-04-23 | 1 | 66 | 66 | 11.9 | 7.4 | 39.1774 | Yes | 70
2025-04-24 | 1.2 | 66 | 79.2 | 10.9 | 7 | 37.2218 | Yes | 70
2025-04-25 | 0.9 | 66 | 59.4 | 12.5 | 7.3 | 35.5566 | Yes | 70
2025-04-26 | 0.9 | 66 | 59.4 | 11.7 | 7.3 | 37.915 | Yes | 70
2025-04-27 | 1.4 | 66 | 92.4 | 11.4 | 7.2 | 39.4827 | Yes | 70
2025-04-28 | 1.3 | 66 | 85.8 | 13.1 | 7.3 | 35.7536 | Yes | 70
2025-04-29 | 1.3 | 66 | 85.8 | 13 | 7.3 | 35.9921 | Yes | 70
2025-04-30 | 1.5 | 66 | 99 | 12.5 | 6.5 | 28.3095 | Yes | 70
2025-05-01 | off | 66 | Off |  |  | Off | Off | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2
Formulas:
Date / Time = [Date / Time, row above]+1