## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-05-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-05-01 |  |  | 0.05 | 0.06 | 0.07 |  | 0.07
2025-05-02 |  |  | 0.05 | 0.07 | 0.08 |  | 0.08
2025-05-03 |  |  | 0.05 | 0.2 | 0.05 |  | 0.2
2025-05-04 |  |  | 0.05 | 0.05 | 0.05 |  | 0.05
2025-05-05 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-05-06 |  |  | 0.05 | 0.05 | 0.05 |  | 0.05
2025-05-07 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-05-08 |  |  | 0.05 | 0.05 | 0.05 |  | 0.05
2025-05-09 |  |  | 0.05 | 0.05 | 0.05 |  | 0.05
2025-05-10 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-05-11 |  |  |  | 0.06 | 0.05 | 0.05 | 0.06
2025-05-12 |  |  |  | 0.06 | 0.07 |  | 0.07
2025-05-13 |  |  |  | 0.05 | 0.07 |  | 0.07
2025-05-14 |  |  |  |  | 0.06 | 0.06 | 0.06
2025-05-15 |  |  |  | 0.06 |  |  | 0.06
2025-05-16 |  |  | 0.06 | 0.06 |  |  | 0.06
2025-05-17 |  |  | 0.04 | 0.11 |  |  | 0.11
2025-05-18 |  |  | 0.05 | 0.1 |  |  | 0.1
2025-05-19 |  |  | 0.09 | 0.09 |  |  | 0.09
2025-05-20 |  |  | 0.08 | 0.16 |  |  | 0.16
2025-05-21 |  |  | 0.07 | 0.09 | 0.08 |  | 0.09
2025-05-22 |  |  | 0.05 | 0.05 | 0.05 |  | 0.05
2025-05-23 |  |  | 0.04 | 0.05 | 0.04 |  | 0.05
2025-05-24 |  |  | 0.04 | 0.05 | 0.05 |  | 0.05
2025-05-25 |  |  | 0.05 | 0.05 | 0.05 |  | 0.05
2025-05-26 |  |  | 0.05 | 0.05 |  |  | 0.05
2025-05-27 |  |  | 0.04 | 0.05 |  |  | 0.05
2025-05-28 |  |  | 0.05 | 0.05 |  |  | 0.05
2025-05-29 |  |  | 0.04 | 0.05 | 0.05 |  | 0.05
2025-05-30 |  |  | 0.05 | 0.05 | 0.04 |  | 0.05
2025-05-31 |  |  | 0.05 | 0.05 | 0.05 |  | 0.05
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE:6/4/2025
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
2025-05-01 | 1.6 | 66 | 105.6 | 11.1 | 7.2 | 41.1751 | Yes | 70
2025-05-02 | 1.4 | 66 | 92.4 | 12.2 | 7.5 | 41.5986 | Yes | 70
2025-05-03 | 1.3 | 66 | 85.8 | 12.6 | 7.5 | 39.7901 | Yes | 70
2025-05-04 | 1.4 | 66 | 92.4 | 12.9 | 7.3 | 36.6456 | Yes | 70
2025-05-05 | 1.3 | 66 | 85.8 | 12 | 7.3 | 38.8748 | Yes | 70
2025-05-06 | 1.2 | 66 | 79.2 | 14.7 | 7.3 | 31.7776 | Yes | 70
2025-05-07 | 1.2 | 66 | 79.2 | 13 | 7.4 | 36.9239 | Yes | 70
2025-05-08 | 1 | 66 | 66 | 13 | 7.2 | 33.5242 | Yes | 70
2025-05-09 | 1.3 | 66 | 85.8 | 13.9 | 7.3 | 33.9005 | Yes | 70
2025-05-10 | 1.2 | 66 | 79.2 | 13.3 | 7.3 | 34.8828 | Yes | 70
2025-05-11 | 1.3 | 66 | 85.8 | 12.2 | 7.2 | 37.0704 | Yes | 70
2025-05-12 | 1.2 | 66 | 79.2 | 11.9 | 7.2 | 37.3805 | Yes | 70
2025-05-13 | 1.3 | 66 | 85.8 | 12.6 | 7 | 33.084 | Yes | 70
2025-05-14 | 1.5 | 66 | 99 | 12.5 | 7 | 34.0711 | Yes | 70
2025-05-15 | 1.4 | 66 | 92.4 | 11.9 | 7 | 35.676 | Yes | 70
2025-05-16 | 1.4 | 66 | 92.4 | 13.1 | 7.5 | 38.9303 | Yes | 70
2025-05-17 | 1 | 66 | 66 | 13 | 7.5 | 37.4521 | Yes | 70
2025-05-18 | 1.5 | 66 | 99 | 12.5 | 6.4 | 27.2768 | Yes | 70
2025-05-19 | 1.6 | 66 | 105.6 | 12.1 | 7.1 | 37.2647 | Yes | 70
2025-05-20 | 1.5 | 66 | 99 | 12 | 6.5 | 30.2541 | Yes | 70
2025-05-21 | 1.1 | 66 | 72.6 | 12.6 | 7 | 32.3397 | Yes | 70
2025-05-22 | 1.3 | 66 | 85.8 | 12.1 | 6.8 | 32.5452 | Yes | 70
2025-05-23 | 1.2 | 66 | 79.2 | 13.5 | 7.1 | 31.9672 | Yes | 70
2025-05-24 | 1.2 | 66 | 79.2 | 14.6 | 7.1 | 29.705 | Yes | 70
2025-05-25 | 1.1 | 66 | 72.6 | 14.5 | 7.1 | 29.5649 | Yes | 70
2025-05-26 | 1.3 | 66 | 85.8 | 14.3 | 7 | 29.5376 | Yes | 70
2025-05-27 | 1.2 | 66 | 79.2 | 14.2 | 7 | 29.3983 | Yes | 70
2025-05-28 | 1.3 | 66 | 85.8 | 14.5 | 6.9 | 28.0832 | Yes | 70
2025-05-29 | 1.1 | 66 | 72.6 | 15.4 | 7 | 26.8226 | Yes | 70
2025-05-30 | 1.2 | 66 | 79.2 | 16.6 | 7 | 25.0341 | Yes | 70
2025-05-31 | 1.4 | 66 | 92.4 | 14.4 | 6.5 | 24.6416 | Yes | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2
Formulas:
Date / Time = [Date / Time, row above]+1