## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-06-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-06-01 |  |  | 0.05 | 0.05 |  |  | 0.05
2025-06-02 |  |  |  | 0.05 | 0.06 |  | 0.06
2025-06-03 |  |  |  | 0.06 | 0.06 |  | 0.06
2025-06-04 |  |  | 0.05 | 0.05 |  |  | 0.05
2025-06-05 |  |  |  | 0.05 | 0.06 |  | 0.06
2025-06-06 |  |  | 0.05 | 0.05 |  |  | 0.05
2025-06-07 |  |  |  | 0.08 | 0.09 |  | 0.09
2025-06-08 |  |  | 0.08 | 0.2 |  |  | 0.2
2025-06-09 |  |  |  | 0.1 | 0.15 |  | 0.15
2025-06-10 |  |  | 0.07 | 0.17 |  |  | 0.17
2025-06-11 |  |  |  | 0.09 |  |  | 0.09
2025-06-12 |  |  |  | 0.09 | 0.06 |  | 0.09
2025-06-13 |  |  | 0.04 | 0.04 | 0.05 | 0.04 | 0.05
2025-06-14 |  |  |  | 0.04 | 0.05 |  | 0.05
2025-06-15 |  |  |  | 0.05 | 0.05 | 0.04 | 0.05
2025-06-16 |  |  |  |  | 0.05 |  | 0.05
2025-06-17 |  |  |  | 0.04 | 0.05 | 0.05 | 0.05
2025-06-18 |  |  |  | 0.04 | 0.05 |  | 0.05
2025-06-19 |  |  |  | 0.05 | 0.09 |  | 0.09
2025-06-20 |  |  |  | 0.05 | 0.09 |  | 0.09
2025-06-21 |  |  | 0.06 | 0.12 |  |  | 0.12
2025-06-22 |  |  |  |  | 0.09 | 0.09 | 0.09
2025-06-23 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-06-24 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-06-25 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-06-26 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-06-27 |  |  |  |  | 0.04 | 0.04 | 0.04
2025-06-28 |  |  |  | 0.04 | 0.04 |  | 0.04
2025-06-29 |  |  | 0.05 | 0.09 | 0.05 |  | 0.09
2025-06-30 |  |  | 0.04 | 0.04 |  |  | 0.04
2025-07-01 | [6 empty] | Off
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE:
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-06-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 66 | 79.2 | 15.7 | 6.9 | 25.6197 | Yes | 70
2 | 1 | 66 | 66 | 17 | 6.6 | 20.5054 | Yes | 70
3 | 1.2 | 66 | 79.2 | 15.1 | 7.3 | 30.9411 | Yes | 70
4 | 1.3 | 66 | 85.8 | 14.3 | 7.2 | 31.8102 | Yes | 70
5 | 1.6 | 66 | 105.6 | 13.8 | 6.8 | 29.344 | Yes | 70
6 | 1.5 | 66 | 99 | 15 | 7 | 28.8385 | Yes | 70
7 | 1 | 66 | 66 | 17.8 | 7.5 | 27.1955 | Yes | 70
8 | 1 | 66 | 66 | 17.9 | 7.4 | 26.0273 | Yes | 70
9 | 1.1 | 66 | 72.6 | 17 | 7.4 | 27.9621 | Yes | 70
10 | 1.3 | 66 | 85.8 | 15.8 | 7.2 | 28.7793 | Yes | 70
11 | 1.5 | 66 | 99 | 16.3 | 6.8 | 24.5374 | Yes | 70
12 | 1.3 | 66 | 85.8 | 16.6 | 7.3 | 28.3124 | Yes | 70
13 | 1.2 | 66 | 79.2 | 15.7 | 7.5 | 32.0131 | Yes | 70
14 | 1.6 | 66 | 105.6 | 15.8 | 6.7 | 24.7283 | Yes | 70
15 | 1.1 | 66 | 72.6 | 17.4 | 7.3 | 26.2293 | Yes | 70
16 | 1.2 | 66 | 79.2 | 16.8 | 7.2 | 26.6106 | Yes | 70
17 | 1.3 | 66 | 85.8 | 14.8 | 7 | 28.567 | Yes | 70
18 | 1.1 | 66 | 72.6 | 15.6 | 7.2 | 28.5083 | Yes | 70
19 | 1 | 66 | 66 | 13.6 | 7.1 | 31.0397 | Yes | 70
20 | 1.2 | 66 | 79.2 | 15.1 | 7.3 | 30.9411 | Yes | 70
21 | 1.2 | 66 | 79.2 | 14.3 | 7 | 29.2025 | Yes | 70
22 | 1.2 | 66 | 79.2 | 14.1 | 7.2 | 31.8723 | Yes | 70
23 | 1.4 | 66 | 92.4 | 15.4 | 7.1 | 28.8089 | Yes | 70
24 | 1.3 | 66 | 85.8 | 15.3 | 7.3 | 30.8808 | Yes | 70
25 | 1.8 | 66 | 118.8 | 14.8 | 6.8 | 28.0803 | Yes | 70
26 | 1.4 | 66 | 92.4 | 15.4 | 7.1 | 28.8089 | Yes | 70
27 | 1.3 | 66 | 85.8 | 16.1 | 7.2 | 28.2078 | Yes | 70
28 | 1.4 | 66 | 92.4 | 15.7 | 7.1 | 28.2368 | Yes | 70
29 | 1.6 | 66 | 105.6 | 15.6 | 6.9 | 27.0001 | Yes | 70
30 | 1.6 | 66 | 105.6 | 16.4 | 6.9 | 25.5906 | Yes | 70
31 | off | 66 | Off |  |  | Off | Off | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2