## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-07-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-07-01 |  |  | 0.08 |  |  |  | 0.08
2025-07-02 |  |  | 0.07 |  |  |  | 0.07
2025-07-03 |  |  | 0.09 |  |  |  | 0.09
2025-07-04 |  |  |  | 0.08 |  |  | 0.08
2025-07-05 |  |  |  | 0.04 |  |  | 0.04
2025-07-06 |  |  | 0.05 |  |  |  | 0.05
2025-07-07 |  |  | 0.07 |  |  |  | 0.07
2025-07-08 |  |  | 0.07 |  |  |  | 0.07
2025-07-09 |  |  | 0.05 |  |  |  | 0.05
2025-07-10 |  |  | 0.04 |  |  |  | 0.04
2025-07-11 |  |  |  | 0.03 |  |  | 0.03
2025-07-12 |  |  | 0.04 |  |  |  | 0.04
2025-07-13 |  |  | 0.04 |  |  |  | 0.04
2025-07-14 |  |  |  | 0.04 |  |  | 0.04
2025-07-15 |  |  |  | 0.04 |  |  | 0.04
2025-07-16 |  |  |  | 0.04 |  |  | 0.04
2025-07-17 |  |  |  | 0.04 |  |  | 0.04
2025-07-18 |  |  |  | 0.04 |  |  | 0.04
2025-07-19 |  |  |  | 0.04 |  |  | 0.04
2025-07-20 |  |  |  | 0.03 |  |  | 0.03
2025-07-21 |  |  |  | 0.04 |  |  | 0.04
2025-07-22 |  |  |  | 0.04 |  |  | 0.04
2025-07-23 |  |  |  |  | 0.06 |  | 0.06
2025-07-24 |  |  |  | 0.04 |  |  | 0.04
2025-07-25 |  |  |  | 0.04 |  |  | 0.04
2025-07-26 |  |  |  |  | 0.06 |  | 0.06
2025-07-27 |  |  |  | 0.04 |  |  | 0.04
2025-07-28 |  |  |  | 0.04 |  |  | 0.04
2025-07-29 |  |  |  | 0.05 |  |  | 0.05
2025-07-30 |  |  |  |  | 0.05 |  | 0.05
2025-07-31 |  |  | 0.08 |  |  |  | 0.08
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE: 8-7-2025
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 66 | 99 | 16.3 | 6.9 | 25.4694 | Yes | 70
2 | 1.6 | 66 | 105.6 | 16.8 | 6.7 | 23.1207 | Yes | 70
3 | 1.4 | 66 | 92.4 | 16 | 7 | 26.6655 | Yes | 70
4 | 1.5 | 66 | 99 | 15.9 | 6.8 | 25.2053 | Yes | 70
5 | 1.2 | 66 | 79.2 | 15.4 | 6.9 | 26.1402 | Yes | 70
6 | 1.6 | 66 | 105.6 | 15.6 | 6.8 | 26.0138 | Yes | 70
7 | 1.2 | 66 | 79.2 | 16.7 | 7.1 | 25.8107 | Yes | 70
8 | 1.1 | 66 | 72.6 | 17.8 | 7.2 | 24.6009 | Yes | 70
9 | 1.3 | 66 | 85.8 | 17 | 7.2 | 26.5586 | Yes | 70
10 | 1.2 | 66 | 79.2 | 17.5 | 7.4 | 27.3528 | Yes | 70
11 | 1.6 | 66 | 105.6 | 17.7 | 6.9 | 23.4509 | Yes | 70
12 | 1.1 | 66 | 72.6 | 20.1 | 7.4 | 22.7102 | Yes | 70
13 | 1.4 | 66 | 92.4 | 20.2 | 7.2 | 21.666 | Yes | 70
14 | 1.5 | 66 | 99 | 18.2 | 7.1 | 24.155 | Yes | 70
15 | 1.1 | 66 | 72.6 | 18.4 | 7.4 | 25.4589 | Yes | 70
16 | 1.3 | 66 | 85.8 | 20.4 | 7.3 | 21.9374 | Yes | 70
17 | 1.4 | 66 | 92.4 | 18 | 7.2 | 25.1221 | Yes | 70
18 | 1.3 | 66 | 85.8 | 17.5 | 7.1 | 24.7436 | Yes | 70
19 | 1.1 | 66 | 72.6 | 19.4 | 7.4 | 23.8053 | Yes | 70
20 | 0.95 | 66 | 62.7 | 17.1 | 7.5 | 28.3372 | Yes | 70
21 | 1.1 | 66 | 72.6 | 16.9 | 7.3 | 27.1228 | Yes | 70
22 | 1.1 | 66 | 72.6 | 19 | 7.2 | 22.6937 | Yes | 70
23 | 1.4 | 66 | 92.4 | 18 | 7.2 | 25.1221 | Yes | 70
24 | 1.4 | 66 | 92.4 | 17.2 | 7.4 | 28.5523 | Yes | 70
25 | 1.4 | 66 | 92.4 | 17.3 | 7.3 | 27.3275 | Yes | 70
26 | 1.3 | 66 | 85.8 | 18.4 | 7.4 | 26.0487 | Yes | 70
27 | 1.2 | 66 | 79.2 | 18.6 | 7.5 | 26.3731 | Yes | 70
28 | 1.2 | 66 | 79.2 | 18.2 | 7.5 | 27.0892 | Yes | 70
29 | 1.2 | 66 | 79.2 | 19.2 | 7.4 | 24.4059 | Yes | 70
30 | 1.1 | 66 | 72.6 | 19.1 | 7.4 | 24.2902 | Yes | 70
31 | 1.1 | 66 | 72.6 | 18.2 | 7.3 | 24.8589 | Yes | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2