## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-08-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-08-01 |  |  |  | 0.04 |  |  | 0.04
2025-08-02 |  |  |  | 0.05 |  |  | 0.05
2025-08-03 |  |  |  | 0.06 |  |  | 0.06
2025-08-04 |  |  |  | 0.09 |  |  | 0.09
2025-08-05 |  |  |  | 0.07 |  |  | 0.07
2025-08-06 |  |  |  | 0.04 |  |  | 0.04
2025-08-07 |  |  |  | 0.04 |  |  | 0.04
2025-08-08 |  |  |  | 0.04 |  |  | 0.04
2025-08-09 |  |  |  | 0.04 |  |  | 0.04
2025-08-10 |  |  |  | 0.04 |  |  | 0.04
2025-08-11 |  |  |  | 0.04 |  |  | 0.04
2025-08-12 |  |  |  | 0.05 |  |  | 0.05
2025-08-13 |  |  |  | 0.04 |  |  | 0.04
2025-08-14 |  |  |  | 0.06 |  |  | 0.06
2025-08-15 |  |  |  | 0.05 |  |  | 0.05
2025-08-16 |  |  |  | 0.09 |  |  | 0.09
2025-08-17 |  |  |  | 0.04 |  |  | 0.04
2025-08-18 |  |  |  | 0.04 |  |  | 0.04
2025-08-19 |  |  |  | 0.04 |  |  | 0.04
2025-08-20 |  |  |  | 0.07 |  |  | 0.07
2025-08-21 |  |  |  | 0.05 |  |  | 0.05
2025-08-22 |  |  |  | 0.04 |  |  | 0.04
2025-08-23 |  |  |  | 0.04 |  |  | 0.04
2025-08-24 |  |  |  | 0.04 |  |  | 0.04
2025-08-25 |  |  |  | 0.04 |  |  | 0.04
2025-08-26 |  |  |  | 0.04 |  |  | 0.04
2025-08-27 |  |  |  | 0.06 |  |  | 0.06
2025-08-28 |  |  |  | 0.05 |  |  | 0.05
2025-08-29 |  |  |  | 0.04 |  |  | 0.04
2025-08-30 |  |  |  | 0.04 |  |  | 0.04
2025-08-31 |  |  |  | 0.04 |  |  | 0.04
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE: 9/4/2025
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 66 | 79.2 | 18.5 | 7.3 | 24.6441 | Yes | 70
2 | 1.1 | 66 | 72.6 | 20 | 7.4 | 22.8636 | Yes | 70
3 | 1.2 | 66 | 79.2 | 18.6 | 7.5 | 26.3731 | Yes | 70
4 | 1.1 | 66 | 72.6 | 17.3 | 7.7 | 30.6345 | Yes | 70
5 | 1.2 | 66 | 79.2 | 18.5 | 7.5 | 26.5504 | Yes | 70
6 | 1.4 | 66 | 92.4 | 17.7 | 7.4 | 27.6131 | Yes | 70
7 | 1.45 | 66 | 95.7 | 18.2 | 7.2 | 24.9296 | Yes | 70
8 | 1.4 | 66 | 92.4 | 16.7 | 7.1 | 26.4084 | Yes | 70
9 | 1.3 | 66 | 85.8 | 19 | 7.1 | 22.3692 | Yes | 70
10 | 1.4 | 66 | 92.4 | 20.8 | 7 | 19.2999 | Yes | 70
11 | 1.2 | 66 | 79.2 | 20.3 | 7 | 19.5082 | Yes | 70
12 | 1.2 | 66 | 79.2 | 18.5 | 7 | 22.0308 | Yes | 70
13 | 1.2 | 66 | 79.2 | 19.4 | 7.1 | 21.5248 | Yes | 70
14 | 1.5 | 66 | 99 | 20 | 7.2 | 22.2144 | Yes | 70
15 | 1.4 | 66 | 92.4 | 19.1 | 7.2 | 23.3323 | Yes | 70
16 | 1.5 | 66 | 99 | 18.5 | 6.8 | 21.1592 | Yes | 70
17 | 1.2 | 66 | 79.2 | 18.2 | 6.9 | 21.6547 | Yes | 70
18 | 1.3 | 66 | 85.8 | 18.9 | 7 | 21.6929 | Yes | 70
19 | 1.3 | 66 | 85.8 | 17.9 | 7.1 | 24.0876 | Yes | 70
20 | 1.3 | 66 | 85.8 | 19.4 | 7.1 | 21.7741 | Yes | 70
21 | 1.3 | 66 | 85.8 | 18.3 | 7.1 | 23.4485 | Yes | 70
22 | 1.4 | 66 | 92.4 | 17.9 | 6.8 | 21.7809 | Yes | 70
23 | 1.2 | 66 | 79.2 | 18.1 | 7.2 | 24.3883 | Yes | 70
24 | 1.2 | 66 | 79.2 | 17.9 | 7.2 | 24.7181 | Yes | 70
25 | 1.3 | 66 | 85.8 | 18 | 7 | 23.049 | Yes | 70
26 | 1.2 | 66 | 79.2 | 17.5 | 7.2 | 25.3907 | Yes | 70
27 | 1.4 | 66 | 92.4 | 17 | 7 | 24.936 | Yes | 70
28 | 1.2 | 66 | 79.2 | 17.8 | 7.2 | 24.8846 | Yes | 70
29 | 1.3 | 66 | 85.8 | 18.6 | 7.1 | 22.9799 | Yes | 70
30 | 1.4 | 66 | 92.4 | 16.7 | 7.1 | 26.4084 | Yes | 70
31 | 1.4 | 66 | 92.4 | 16.5 | 7.1 | 26.7647 | Yes | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2