## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-12-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2025-12-01 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-12-02 |  |  |  | 0.05 |  |  | 0.05
2025-12-03 |  |  |  | 0.04 |  |  | 0.04
2025-12-04 |  |  |  | 0.05 |  |  | 0.05
2025-12-05 |  |  |  | 0.161 |  |  | 0.161
2025-12-06 | [6 empty] | Off
2025-12-07 | [6 empty] | Off
2025-12-08 |  |  |  | 0.05 | 0.05 |  | 0.05
2025-12-09 | [6 empty] | Off
2025-12-10 | [6 empty] | Off
2025-12-11 | [6 empty] | Off
2025-12-12 | [6 empty] | Off
2025-12-13 | [6 empty] | Off
2025-12-14 | [6 empty] | Off
2025-12-15 |  |  |  | 0.07 | 0.04 | 0.04 | 0.07
2025-12-16 | [6 empty] | Off
2025-12-17 | [6 empty] | Off
2025-12-18 |  |  |  | 0.09 | 0.08 |  | 0.09
2025-12-19 | [6 empty] | Off
2025-12-20 | [6 empty] | Off
2025-12-21 | [6 empty] | Off
2025-12-22 | [6 empty] | Off
2025-12-23 | [6 empty] | Off
2025-12-24 | [6 empty] | Off
2025-12-25 | [6 empty] | Off
2025-12-26 | [6 empty] | Off
2025-12-27 | [6 empty] | Off
2025-12-28 | [6 empty] | Off
2025-12-29 |  |  |  | 0.09 |  |  | 0.09
2025-12-30 |  |  |  | 0.161 |  |  | 0.161
2025-12-31 |  |  |  | 0.08 |  |  | 0.08
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE: 1-6-2026
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2025-12-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 66 | 79.2 | 12 | 6.8 | 32.3984 | Yes | 70
2 | 1.1 | 66 | 72.6 | 12.3 | 6.8 | 31.4462 | Yes | 70
3 | 1.1 | 66 | 72.6 | 11.7 | 6.9 | 33.7919 | Yes | 70
4 | 1.2 | 66 | 79.2 | 13.2 | 6.5 | 26.1025 | Yes | 70
5 | 1.1 | 66 | 72.6 | 13.5 | 6.6 | 26.251 | Yes | 70
6 | off | 66 | Off |  |  | Off | Off | 70
7 | off | 66 | Off |  |  | Off | Off | 70
8 | 1.3 | 66 | 85.8 | 13.5 | 6.7 | 27.8759 | Yes | 70
9 | off | 66 | Off |  |  | Off | Off | 70
10 | off | 66 | Off |  |  | Off | Off | 70
11 | off | 66 | Off |  |  | Off | Off | 70
12 | off | 66 | Off |  |  | Off | Off | 70
13 | off | 66 | Off |  |  | Off | Off | 70
14 | off | 66 | Off |  |  | Off | Off | 70
15 | 1.3 | 66 | 85.8 | 12.9 | 6.5 | 26.939 | Yes | 70
16 | off | 66 | Off |  |  | Off | Off | 70
17 | off | 66 | Off |  |  | Off | Off | 70
18 | 1.2 | 66 | 79.2 | 11.6 | 7.1 | 36.8218 | Yes | 70
19 | off | 66 | Off |  |  | Off | Off | 70
20 | off | 66 | Off |  |  | Off | Off | 70
21 | off | 66 | Off |  |  | Off | Off | 70
22 | off | 66 | Off |  |  | Off | Off | 70
23 | off | 66 | Off |  |  | Off | Off | 70
24 | off | 66 | Off |  |  | Off | Off | 70
25 | off | 66 | Off |  |  | Off | Off | 70
26 | off | 66 | Off |  |  | Off | Off | 70
27 | off | 66 | Off |  |  | Off | Off | 70
28 | off | 66 | Off |  |  | Off | Off | 70
29 | 1.3 | 66 | 85.8 | 10.9 | 6.3 | 29.6753 | Yes | 70
30 | 1.1 | 66 | 72.6 | 9.6 | 6.6 | 34.8936 | Yes | 70
31 | 1.4 | 66 | 92.4 | 9.1 | 6.6 | 37.2482 | Yes | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2