## Page 1
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-01-01
System Name: | Beaver Water District |  |  | ID#: 4100199 |  |  | WTP : TP - | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
2026-01-01 |  |  |  | 0.085 |  |  | 0.085
2026-01-02 |  |  |  | 0.045 |  |  | 0.045
2026-01-03 |  |  |  | 0.04 |  |  | 0.04
2026-01-04 |  |  |  | 0.09 |  |  | 0.09
2026-01-05 |  |  |  | 0.04 |  |  | 0.04
2026-01-06 |  |  |  | 0.04 |  |  | 0.04
2026-01-07 |  |  |  | 0.04 |  |  | 0.04
2026-01-08 |  |  |  | 0.07 |  |  | 0.07
2026-01-09 |  |  |  | 0.184 |  |  | 0.184
2026-01-10 |  |  |  | 0.139 |  |  | 0.139
2026-01-11 |  |  |  | 0.133 |  |  | 0.133
2026-01-12 |  |  |  | 0.09 |  |  | 0.09
2026-01-13 |  |  |  | 0.08 |  |  | 0.08
2026-01-14 |  |  |  | 0.12 |  |  | 0.12
2026-01-15 |  |  |  | 0.13 |  |  | 0.13
2026-01-16 |  |  |  | 0.18 |  |  | 0.18
2026-01-17 |  |  |  | 0.04 |  |  | 0.04
2026-01-18 |  |  |  | 0.06 |  |  | 0.06
2026-01-19 |  |  |  | 0.03 |  |  | 0.03
2026-01-20 |  |  |  | 0.04 |  |  | 0.04
2026-01-21 |  |  |  | 0.06 |  |  | 0.06
2026-01-22 |  |  |  | 0.06 |  |  | 0.06
2026-01-23 |  |  |  | 0.06 |  |  | 0.06
2026-01-24 |  |  |  | 0.1 |  |  | 0.1
2026-01-25 |  |  |  | 0.12 |  |  | 0.12
2026-01-26 |  |  |  | 0.09 |  |  | 0.09
2026-01-27 |  |  |  | 0.13 |  |  | 0.13
2026-01-28 |  |  |  | 0.1 |  |  | 0.1
2026-01-29 |  |  |  | 0.08 |  |  | 0.08
2026-01-30 |  |  |  | 0.08 |  |  | 0.08
2026-01-31 |  |  |  | 0.03 |  |  | 0.03
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No) Rev. 7-3-24 L.J.C
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Larry J Chitwood
[5 empty] | SIGNATURE: Larry Chitwood |  |  | DATE: 2-2-2026
[5 empty] | PHONE #: (503)801-3338 |  |  | CERT #: 549298
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not correspond to continuous readings' maximum. 2 Filtered systems only. (333-061-0040(1)(d)(B&C))
Page 1 of 2
Formulas:
System Name: = [System Name:, row above]+1

## Page 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | WTP-A
System Name: Beaver Water District |  |  | ID#: 4100199 |  | Month/Year: | 2026-01-01 | Disinfection Giardia Log Inactiv: | 1
\
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.3 | 66 | 85.8 | 9.7 | 6.6 | 35.4411 | Yes | 70
2 | 1 | 66 | 66 | 10.7 | 7.3 | 40.9211 | Yes | 70
3 | 1.1 | 66 | 72.6 | 10.9 | 7.2 | 39.4475 | Yes | 70
4 | 1.8 | 66 | 118.8 | 11.1 | 7 | 39.2754 | Yes | 70
5 | 1.8 | 66 | 118.8 | 10.4 | 6.9 | 39.7055 | Yes | 70
6 | 1.7 | 66 | 112.2 | 10.1 | 6.9 | 40.0404 | Yes | 70
7 | 1.6 | 66 | 105.6 | 10.2 | 6.5 | 34.2806 | Yes | 70
8 | 1.4 | 66 | 92.4 | 10.4 | 6.6 | 34.2596 | Yes | 70
9 | 1.3 | 66 | 85.8 | 10.8 | 6.5 | 31.9348 | Yes | 70
10 | 1.5 | 66 | 99 | 10.6 | 6.6 | 34.1966 | Yes | 70
11 | 1.4 | 66 | 92.4 | 10.6 | 6.7 | 34.998 | Yes | 70
12 | 1.3 | 66 | 85.8 | 10.8 | 6.7 | 34.1756 | Yes | 70
13 | 1.2 | 66 | 79.2 | 10.5 | 6.8 | 35.6571 | Yes | 70
14 | 1.5 | 66 | 99 | 10.6 | 6.4 | 31.9542 | Yes | 70
15 | 1.3 | 66 | 85.8 | 10.1 | 6.6 | 34.5431 | Yes | 70
16 | 1.1 | 66 | 72.6 | 10.5 | 6.9 | 36.4976 | Yes | 70
17 | 1.3 | 66 | 85.8 | 10.7 | 6.8 | 35.5912 | Yes | 70
18 | 1.3 | 66 | 85.8 | 9.6 | 6.9 | 39.5604 | Yes | 70
19 | 1.2 | 66 | 79.2 | 9.1 | 7.2 | 44.8968 | Yes | 70
20 | 1.5 | 66 | 99 | 9.4 | 6.3 | 33.3374 | Yes | 70
21 | 1.2 | 66 | 79.2 | 8.1 | 6.9 | 43.1583 | Yes | 70
22 | 1.1 | 66 | 72.6 | 7.5 | 7.1 | 47.6448 | Yes | 70
23 | 1 | 66 | 66 | 8.3 | 7.4 | 49.679 | Yes | 70
24 | 1.1 | 66 | 72.6 | 7 | 7.2 | 51.0442 | Yes | 70
25 | 0.9 | 66 | 59.4 | 6.4 | 7.5 | 57.8362 | Yes | 70
26 | 1.2 | 66 | 79.2 | 7.3 | 7.4 | 54.3577 | Yes | 70
27 | 1 | 66 | 66 | 7.5 | 7.7 | 58.3748 | Yes | 70
28 | 1.3 | 66 | 85.8 | 9.5 | 6.5 | 34.692 | Yes | 70
29 | 1.4 | 66 | 92.4 | 9.7 | 6.6 | 35.8336 | Yes | 70
30 | 1.4 | 66 | 92.4 | 10 | 6.6 | 35.1491 | Yes | 70
31 | 1.3 | 66 | 85.8 | 10.1 | 6.5 | 33.3869 | Yes | 70
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
Return by 10th of following month by email, fax, or mail to:
dwp.dmce@odhsoha.oregon.gov 971-673-0694; or, OHA-Drinking Water Services, PO Box 14450, Portland, OR 97293-0450
Page 2 Of 2