## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackmas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-02-21
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.26 | 0.28 |  |  | 0.28
2 |  |  | 0.28 | 0.28 |  |  | 0.28
3 | [5 empty] | 0.24 | 0.247
4 | 0.22 | 0.22 |  |  |  |  | 0.22
5 |  |  | ..24 | 0.24 |  |  | 0.24
6 |  |  | 0.24 | 0.24 |  |  | 0.24
7 |  |  | 0.24 | 0.24 |  |  | 0.26
8 | [5 empty] | 0.26 | 0.26
9 | 0.26 |  |  | 0.28 |  |  | 0.28
10 |  |  | 0.26 | 0.26 |  |  | 0.26
11 |  |  | 0.26
12 |  |  |  | 0.26 | power |  | 0.26
13 |  |  | out
14 | [5 empty] | 0.24 | 0.24
15 | 0.24 | 0.26 | 0.26 | 0.26 |  |  | 0.26
16 |  |  | 0.24 | 0.24 |  |  | 0.24
17 |  |  |  |  | 0.26 |  | 0.26
18 |  |  |  |  | 0.24 |  | 0.24
19 |  |  | 0.24 | 0.24 |  |  | 0.24
20
21 |  |  | 0.24 | 0.24 |  |  | 0.24
22 |  |  |  |  | 0.24 | 0.26 | 0.26
23 |  |  | 0.24 | 0.24 |  |  | 0.24
24 |  |  |  |  | 0.22 | 0.22 | 0.22
25 | 0.22 | [5 empty] | 0.22
26 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
27 |  |  |  | 0.22 | 0.22 |  | 0.222
28 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summay (answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | YES |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Notes: |  |  |  |  | SIGNATURE: Pete Dostert --6574
1 2
including continuous NTU data, if applicable. |  |  |  |  | IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C)

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | COLTON WATER DISTRICT |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2021-02-01 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
145
1 |  | 175 | 35 | 0 |  |  |  |  | 1.03 | 200 | 50 | 51.5 | 7 | 7 | 47.1635 | 109.1947 | 109.1947 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.04 | 140 | 50 | 52 | 7 | 7 | 47.2172 | 110.1294 | 110.1294 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.05 | 145 | 50 | 52.5 | 7 | 7 | 47.2709 | 111.0619 | 111.0619 | yes
4 |  |  | 35 | 0 |  |  |  | . | 1.02 | 210 | 50 | 51 | 7 | 6 | 50.3566 | 101.2778 | 148 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.01 | 200 | 50 | 50.5 | 7 | 6 | 50.2989 | 100.3997 | 100.3997 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.04 | 160 | 50 | 52 | 7 | 6 | 50.472 | 103.0274 | 103.0274 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.05 | 175 | 50 | 52.5 | 7 | 6 | 50.5298 | 103.899 | 103.899 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.04 | 180 | 50 | 52 | 7 | 6 | 50.472 | 103.0274 | 103.0274 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.02 | 145 | 50 | 51 | 7 | 6 | 50.3566 | 101.2778 | 101.2778 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.01 | 180 | 50 | 50.5 | 6.9 | 6 | 48.5416 | 104.0345 | 104.0345 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.04 | 140 | 50 | 52 | 6.9 | 6 | 48.708 | 106.7586 | 106.7586 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.05 | 170 | 50 | 52.5 | 6.9 | 6 | 48.7637 | 107.6622 | 107.6622 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.05 | 130 | 50 | 52.5 | 6.9 | 6 | 48.7637 | 107.6622 | 107.6622 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.04 | 120 | 50 | 52 | 6.9 | 6 | 48.708 | 106.7586 | 106.7586 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.03 | 140 | 50 | 51.5 | 6.9 | 6 | 48.6525 | 105.8528 | 105.8528 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.03 | 160 | 50 | 51.5 | 6.9 | 6 | 48.6525 | 105.8528 | 105.8528 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.05 | 145 | 50 | 52.5 | 6.9 | 6 | 48.7637 | 107.6622 | 107.6622 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.07 | 150 | 50 | 53.5 | 6.9 | 7 | 45.7327 | 116.9841 | 116.9841 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.06 | 200 | 50 | 53 | 6.9 | 7 | 45.6809 | 116.0223 | 116.0223 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.08 | 210 | 50 | 54 | 6.9 | 7 | 45.7846 | 117.9436 | 117.9436 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.07 | 180 | 50 | 53.5 | 7 | 6 | 50.6457 | 105.6358 | 105.6358 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.04 | 195 | 50 | 52 | 7 | 6 | 50.472 | 103.0274 | 103.0274 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.03 | 145 | 50 | 51.5 | 7 | 6 | 50.4142 | 102.1537 | 102.1537 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.02 | 135 | 50 | 51 | 7 | 6 | 50.3566 | 101.2778 | 101.2778 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.05 | 140 | 50 | 52.5 | 7 | 6 | 50.5298 | 103.899 | 103.899 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.04 | 160 | 50 | 52 | 7 | 6 | 50.472 | 103.0274 | 103.0274 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.01 | 170 | 50 | 50.5 | 7 | 6 | 50.2989 | 100.3997 | 100.3997 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.02 | 195 | 50 | 51 | 7.0. | 6 | #VALUE! | 101 | 101 | yes
29 |  |  | 35 | 0 | [6 empty] | 50 | 0
30 |  |  | 35 | 0 | [5 empty] | . | 50 | 0
31 |  |  | 35 | 0 | [6 empty] | 50 | 0
SIGNATURE: PETE DOSTERT/COLTON WATER DISTRICT
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel