## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-03-21
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.254 | 0.26 | 0.26 |  | 0.26
2
3 |  |  | 0.26 | 0.26 | 0.24 |  | 0.26
4
5 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
6
7 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
8
9 |  |  | 0.22 | 0.24 | 0.22 |  | 0.24
10
11 |  |  | 0.222 | 0.22 | 0.22 |  | 0.22
12 |  |  | 0.22 | 0.22 |  |  | 0.22
13 |  | 0.22 | 0.24 |  |  |  | 0.24
14
15 |  |  |  | 0.24 | 0.24 | 0.24 | 0.24
16 | 0.26 | [5 empty] | 0.26
17 |  |  |  | 0.22 | 0.24 |  | 0.24
18
19 |  |  |  | 0.22 | 0.22 | 0.26 | 0.26
20
21 |  |  | 0.24 | 0.216 | 0.26 |  | 0.26
22
23 |  |  |  | 0.24 | 0.24 | 0.256 | 0.26
24 | 0.24 | [5 empty] | 0.24
25 |  |  |  | 0.26 | 0.26 | 0.24 | 0.26
26
27 |  |  | 0.24 | 0.24 |  |  | 0.24
28
29 |  |  | 0.26 | 0.26 | 0.24 | 0.24 | 0.26
30
31 |  |  | 0.28 | 0.26 | 0.24 |  | 0.28
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2021-03-01 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 225 | 35 | 0 |  |  |  |  | 1.07 | 145 | 50 | 53.5 | 7 | 7 | 47.3786 | 112.9201 | 112.9201 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.02 | 180 | 50 | 51 | 7 | 7 | 47.1099 | 108.2576 | 108.2576 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.04 | 190 | 50 | 52 | 7 | 7 | 47.2172 | 110.1294 | 110.1294 | yes
4 |  |  | 35 | 0 |  |  |  |  | 0.99 | 210 | 50 | 49.5 | 7 | 7 | 46.9494 | 105.4327 | 105.4327 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.06 | 200 | 50 | 53 | 7 | 7 | 47.3247 | 111.9921 | 111.9921 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.01 | 200 | 50 | 50.5 | 7.1 | 7 | 48.7547 | 103.5797 | 103.5797 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.07 | 180 | 50 | 53.5 | 7.1 | 7 | 49.0899 | 108.9838 | 108.9838 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.02 | 140 | 50 | 51 | 7.1 | 7 | 48.8104 | 104.4859 | 104.4859 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.06 | 165 | 50 | 53 | 7.1 | 7 | 49.0338 | 108.0886 | 108.0886 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.03 | 170 | 50 | 51.5 | 7.1 | 7 | 48.8662 | 105.3899 | 105.3899 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.1 | 140 | 50 | 55 | 7.1 | 7 | 49.2584 | 111.6561 | 111.6561 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.09 | 200 | 50 | 54.5 | 7.1 | 7 | 49.2021 | 110.7675 | 110.7675 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.09 | 180 | 50 | 54.5 | 7.1 | 7 | 49.2021 | 110.7675 | 110.7675 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.04 | 175 | 50 | 52 | 7.1 | 7 | 48.922 | 106.2917 | 106.2917 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.05 | 140 | 50 | 52.5 | 7.1 | 6 | 52.3661 | 100.2558 | 100.2558 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.2 | 150 | 50 | 60 | 7.1 | 6 | 53.277 | 112.619 | 112.619 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.1 | 180 | 50 | 55 | 7.1 | 6 | 52.6678 | 104.4281 | 104.4281 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.12 | 210 | 50 | 56 | 7.1 | 6 | 52.789 | 106.0827 | 106.0827 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.15 | 185 | 50 | 57.5 | 7.1 | 6 | 52.9714 | 108.5491 | 108.5491 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.16 | 170 | 50 | 58 | 7.1 | 6 | 53.0324 | 109.3671 | 109.3671 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.09 | 140 | 50 | 54.5 | 7 | 6 | 50.7619 | 107.3641 | 107.3641 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.07 | 145 | 50 | 53.5 | 7 | 6 | 50.6457 | 105.6358 | 105.6358 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.09 | 185 | 50 | 54.5 | 7 | 6 | 50.7619 | 107.3641 | 107.3641 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.11 | 200 | 50 | 55.5 | 7 | 6 | 50.8783 | 109.0838 | 109.0838 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.15 | 200 | 50 | 57.5 | 7 | 6 | 51.1121 | 112.4978 | 112.4978 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.16 | 1470 | 50 | 58 | 7 | 6 | 51.1707 | 113.346 | 113.346 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.17 | 180 | 50 | 58.5 | 7 | 6 | 51.2294 | 114.1922 | 114.1922 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.25 | 140 | 50 | 62.5 | 7 | 6 | 51.7017 | 120.8858 | 120.8858 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.18 | 50 | 50 | 59 | 7 | 6 | 51.2882 | 115.0362 | 115.0362 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.24 | 190 | 50 | 62 | 7 | 6 | 51.6424 | 120.0564 | 120.0564 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.22 | 210 | 50 | 61 | 7 | 6 | 51.524 | 118.3913 | 118.3913 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel