## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-06-21
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.2 |  | 0.2 |  | 0.2
2 | 0.22 |  |  | 0.2 |  | 0.2 | 0.2
3 |  |  | 0.22 |  | 0.2 |  | 0.2
4 | 0.2 |  |  | 0.2 |  |  | 0.2
5 |  |  |  | 0.2 |  |  | 0.2
6 |  |  | 0.2 | 0.2 |  | 0.26 | 0.26
7 |  | 0.22 |  |  |  |  | 0.22
8 |  |  | 0.2 | 0.2 | 0.18 | 0.18 | 0.2
9
10 |  |  | 0.2 | 0.2 | 0.22 | 0.22 | 0.22
11 |  |  | 0.22 | 0.22 | 0.2 |  | 0.22
12 |  |  | 0.2 | 0.2 |  |  | 0.2
13 |  | 0.2 | 0.2 | 0.22 |  |  | 0.22
14 | 0.2 | 0.2 | 0.2 |  |  | 0.2 | 0.2
15 | 0.2 |  |  | 0.22 | 0.22 | 0.2 | 0.2
16 |  |  | 0.18 | 0.18 | 0.16 |  | 0.18
17 |  |  | 0.14 | 0.14 | 0.18 | 0.2 | 0.2
18 |  |  | 0.18 | 0.2 | 0.2 | 0.18 | 0.2
19 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
20 |  |  |  | 0.26 | 0.26 | 0.26 | 0.26
21 |  |  | 0.28 | 0.28 | 0.26 | 0.26 | 0.28
22 |  |  | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
23 |  |  |  | 0.26 | 0.26 | 0.26 | 0.26
24 | 0.26 | [5 empty] | 0.26
25 |  | 0.22 | 0.24 | 0.24 | 0.22 | 0.22 | 0.24
26 | 0.22 |  | 0.24 | 0.26 | 0.24 | 0.24 | 0.26
27 | 0.24 | 0.24 | 0.22 | 0.22 | 0.24 | 0.24 | 0.24
28 |  |  | 0.22 | 0.24 | 0.26 | 0.26 | 0.26
29 |  |  | 0.26 | 0.26 | 0.28 | 0.26 | 0.28
30 | 0.28 |  | 0.26 | 0.26 | 0.26 |  | 0.28
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2021-06-21 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  |  | 35 | 0 |  |  |  |  | 1.09 | 220 | 50 | 54.5 | 6.9 | 9 | 40.1857 | 135.6203 | 135.6203 | yes
2 |  | 200 | 35 | 0 |  |  |  |  | 1.07 | 200 | 50 | 53.5 | 6.9 | 9 | 40.096 | 133.4298 | 133.4298 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.07 | 180 | 50 | 53.5 | 6.9 | 9 | 40.096 | 133.4298 | 133.4298 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.05 | 175 | 50 | 52.5 | 7 | 9 | 41.4252 | 126.7343 | 126.7343 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.05 | 165 | 50 | 52.5 | 7 | 9 | 41.4252 | 126.7343 | 126.7343 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.06 | 140 | 50 | 53 | 7 | 9 | 41.4718 | 127.7978 | 127.7978 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.05 | 185 | 50 | 52.5 | 7 | 9 | 41.4252 | 126.7343 | 126.7343 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.07 | 170 | 50 | 53.5 | 7 | 9 | 41.5183 | 128.8587 | 128.8587 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.116 | 150 | 50 | 55.8 | 7 | 9 | 41.7333 | 133.7061 | 133.7061 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.11 | 165 | 50 | 55.5 | 7 | 10 | 39.0676 | 142.0616 | 142.0616 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.012 | 180 | 50 | 50.6 | 7 | 10 | 38.6435 | 130.9405 | 130.9405 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.09 | 190 | 50 | 54.5 | 7.3 | 10 | 43.2811 | 125.9211 | 125.9211 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.08 | 195 | 50 | 54 | 7 | 10 | 38.9372 | 138.6849 | 138.6849 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.05 | 210 | 50 | 52.5 | 7.3 | 10 | 43.0864 | 121.8483 | 121.8483 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1 | 200 | 50 | 50 | 7 | 10 | 38.5919 | 129.5608 | 129.5608 | yes
16 |  |  | 35 | 0 |  |  |  |  | 0.99 | 205 | 50 | 49.5 | 7 | 10 | 38.549 | 128.408 | 128.408 | yes
17 |  |  | 35 | 0 |  |  |  |  | 0.98 | 190 | 50 | 49 | 7 | 10 | 38.5061 | 127.2524 | 127.2524 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.01 | 230 | 50 | 50.5 | 7 | 10 | 38.6349 | 130.7109 | 130.7109 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.02 | 240 | 50 | 51 | 7 | 10 | 38.6779 | 131.8582 | 131.8582 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.04 | 240 | 50 | 52 | 7 | 10 | 38.7641 | 134.1447 | 134.1447 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.05 | 250 | 50 | 52.5 | 7 | 10 | 38.8073 | 135.2838 | 135.2838 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.03 | 280 | 50 | 51.5 | 7 | 10 | 38.721 | 133.0028 | 133.0028 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.01 | 300 | 50 | 50.5 | 7 | 11 | 36.2134 | 139.4512 | 139.4512 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1 | 240 | 50 | 50 | 7.1 | 11 | 37.4402 | 133.5463 | 133.5463 | yes
25 |  |  | 35 | 0 |  |  |  |  | 0.99 | 280 | 50 | 49.5 | 7.1 | 11 | 37.3987 | 132.3574 | 132.3574 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.01 | 350 | 50 | 50.5 | 7.1 | 11 | 37.4817 | 134.7323 | 134.7323 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.01 | 380 | 50 | 50.5 | 7.1 | 11 | 37.4817 | 134.7323 | 134.7323 | yes
28 |  |  | 35 | 0 |  |  |  |  | 0.98 | 375 | 50 | 49 | 7.1 | 12 | 35.0257 | 139.8971 | 139.8971 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.01 | 330 | 50 | 50.5 | 7.1 | 12 | 35.1414 | 143.7051 | 143.7051 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.02 | 300 | 50 | 51 | 7.1 | 12 | 35.1801 | 144.9685 | 144.9685 | yes
31 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel