## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | Clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-08-21
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.26 | 0.26 |  | 0.26 | 0.26
2 | 0.24 |  |  |  | 0.24 | 0.24 | 0.24
3 |  |  |  | 0.24 | 0.22 | 0.22 | 0.24
4 |  | 0.22 | 0.22 | 0.24 |  |  | 0.24
5 |  | 0.22 | 0.22 | 0.2 |  |  | 0.22
6 |  |  | 0.26 | 0.24 | 0.26 |  | 0.26
7 |  |  |  | 0.24 | 0.24 | 0.24 | 0.24
8 |  |  | 0.22 | 0.24 | 0.24 |  | 0.24
9
10 |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
11 |  | 0.26 | 0.26 | 0.26 | 0.26 |  | 0.26
12 |  | 0.22 | 0.22 | 0.22 |  |  | 0.22
13 | 0.22 |  |  | 0.22 | 0.22 | 0.24 | 0.24
14 |  |  | 0.24 | 0.22 | 0.2 |  | 0.24
15 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
16 |  | 0.2 | 0.22 | 0.22 |  |  | 0.22
17 |  |  | 0.24 | 0.24 | 0.22 |  | 0.24
18 |  |  | 0.22 | 0.2 | 0.2 |  | 0.22
19 |  |  | 0.24 | 0.22 | 0.22 | 0.22 | 0.24
20
21 |  |  | 0.24 | 0.24 | .24. | 0.26 | 0.26
22 | 0.26 |  |  |  | 0.24 |  | 0.24
23 |  |  | 0.22 | 0.22 | 0.24 | 0.24 | 0.24
24 |  |  |  | 0.22 | 0.2 |  | 0.22
25 |  |  | 0.2 | 0.2 | 0.22 | 0.22 | 0.22
26 |  | 0.24 | 0.22 | 0.22 | 0.22 |  | 0.24
27 |  | 0.22 | 0.24 | 0.24 |  |  | 0.24
28 |  |  | 0.22 | 0.22 | 0.24 |  | 0.24
29 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
30 | 0.22 |  |  | 0.24 | 0.24 |  | 0.24
31 |  | 0.22 | 0.24 |  |  |  | 0.24
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2021-08-21 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 200 | 35 | 0 |  |  |  |  | 0.99 | 280 | 50 | 49.5 | 7 | 14 | 29.8604 | 165.7713 | 165.7713 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1 | 260 | 50 | 50 | 7 | 14 | 29.8925 | 167.2663 | 167.2663 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.02 | 240 | 50 | 51 | 7 | 14 | 29.9567 | 170.2459 | 170.2459 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.01 | 300 | 50 | 50.5 | 7 | 14 | 29.9245 | 168.7578 | 168.7578 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.03 | 270 | 50 | 51.5 | 7.1 | 14 | 31.0103 | 166.0739 | 166.0739 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.05 | 280 | 50 | 52.5 | 7.1 | 14 | 31.0773 | 168.9336 | 168.9336 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.04 | 345 | 50 | 52 | 7.1 | 14 | 31.0438 | 167.5054 | 167.5054 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.01 | 330 | 50 | 50.5 | 7.1 | 14 | 30.9434 | 163.201 | 163.201 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.07 | 330 | 50 | 53.5 | 7.1 | 14 | 31.1445 | 171.78 | 171.78 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.08 | 320 | 50 | 54 | 7.1 | 14 | 31.1781 | 173.1983 | 173.1983 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.09 | 340 | 50 | 54.5 | 7.1 | 14 | 31.2118 | 174.6133 | 174.6133 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.1 | 370 | 50 | 55 | 7.1 | 14 | 31.2456 | 176.025 | 176.025 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.09 | 360 | 50 | 54.5 | 7.1 | 14 | 31.2118 | 174.6133 | 174.6133 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.08 | 300 | 50 | 54 | 7 | 14 | 30.1503 | 179.1028 | 179.1028 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.06 | 310 | 50 | 53 | 7.1 | 14 | 31.1109 | 170.3585 | 170.3585 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1 | 270 | 50 | 50 | 7 | 14 | 29.8925 | 167.2663 | 167.2663 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1 | 220 | 50 | 50 | 7 | 14 | 29.8925 | 167.2663 | 167.2663 | yes
18 |  |  | 35 | 0 |  |  |  |  | 0.99 | 230 | 50 | 49.5 | 7 | 14 | 29.8604 | 165.7713 | 165.7713 | yes
19 |  |  | 35 | 0 |  |  |  |  | 0.97 | 255 | 50 | 48.5 | 7 | 14 | 29.7964 | 162.7712 | 162.7712 | yes
20 |  |  | 35 | 0 |  |  |  |  | 0.97 | 310 | 50 | 48.5 | 7 | 14 | 29.7964 | 162.7712 | 162.7712 | yes
21 |  |  | 35 | 0 |  |  |  |  | 0.99 | 280 | 50 | 49.5 | 7 | 14 | 29.8604 | 165.7713 | 165.7713 | yes
22 |  |  | 35 | 0 |  |  |  |  | 0.98 | 270 | 50 | 49 | 7 | 14 | 29.8284 | 164.273 | 164.273 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.01 | 195 | 50 | 50.5 | 7 | 14 | 29.9245 | 168.7578 | 168.7578 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1 | 220 | 50 | 50 | 7 | 14 | 29.8925 | 167.2663 | 167.2663 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.02 | 235 | 50 | 51 | 7 | 15 | 28.1461 | 181.1973 | 181.1973 | yes
26 |  |  | 35 | 0 |  |  |  |  | 0.99 | 240 | 50 | 49.5 | 7 | 15 | 28.0566 | 176.4289 | 176.4289 | yes
27 |  |  | 35 | 0 |  |  |  |  | 0.98 | 240 | 50 | 49 | 7 | 15 | 28.0269 | 174.8322 | 174.8322 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.02 | 250 | 50 | 51 | 6.9 | 15 | 27.2339 | 187.2663 | 187.2663 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.01 | 260 | 50 | 50.5 | 6.9 | 15 | 27.2052 | 185.6262 | 185.6262 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1 | 240 | 50 | 50 | 6.9 | 15 | 27.1765 | 183.9823 | 183.9823 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.02 | 230 | 50 | 51 | 6.9 | 15 | 27.2339 | 187.2663 | 187.2663 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel