## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackmas
[7 empty] | clackmas | 2021-11-20
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
2 |  |  | 0.24 | 0.22 | 0.24 |  | 0.22
3 |  | 0.22 | 0.24 |  |  | 0.24 | 0.24
4 |  |  | 0.26 | 0.26 | 0.22 |  | 0.26
5 |  |  | 0.24 | 0.324 |  | 0.24 | 0.24
6 | 0.22 |  |  | 0.22 | 0.22 |  | 0.22
7 |  | 0.22 | 0.22 | 0.2 |  |  | 0.22
8 |  | 0.22 | 0.22 | 0.22 |  |  | 0.22
9 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
10 |  | 0.26 | 0.28 |  |  |  | 0.28
11
12 |  |  | 0.3 | 0.302 | 0.28 |  | 0.3
13 |  |  | 0.3 |  |  |  | 0.3
14 |  |  | 0.3 | 0.28 |  |  | 0.3
15 |  |  | 0.3 | 0.3 | 0.28 | 0.28 | 0.3
16 |  |  | 0.28 | 0.28 | 0.26 |  | 0.283
17 | 0.24 | 0.24 |  |  |  | 0.2 | 0.28
18 |  |  | 0.22 | 0.22 |  |  | 0.22
19 | 0.22 |  | 0.24 | 0.22 | 0.24 |  | 0.24
20 |  |  | 0.26 |  |  |  | 0.26
21 |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
22 |  |  |  | 0.24 | 0.22 | 0.22 | 0.24
23 |  |  | 0.22 | 0.22 |  |  | 0.22
24 |  | 0.22 | 0.22 | 0.22 |  |  | 0.22
25 |  |  | 0.22 | 0.22 |  |  | 0.22
26 | 0.26 |  | 0.28 | 0.28 |  |  | 0.28
27 |  |  | 0.26 | 0.26 | 0.3 |  | 0.302
28
29 |  |  | 0.3 | 0.24 | 0.24 | 0.24 | 0.3
30 |  |  | 0.24 | 0.24 |  |  | 0.24
31
0.24 |  |  |  |  | 0.26
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | yes |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Notes: |  |  |  |  | peter dostert 6574

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | colton water district |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2021-11-20 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
225
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
0.87
1 |  | 200 | 35 | 0 |  |  |  |  | 1.11 | 180 | 50 | 55.5 | 7 | 10 | 39.0676 | 142.0616 | 142.0616 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.12 | 170 | 50 | 56 | 7 | 10 | 39.1111 | 143.1818 | 143.1818 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.11 | 200 | 50 | 55.5 | 7 | 10 | 39.0676 | 142.0616 | 142.0616 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.13 | 145 | 50 | 56.5 | 7 | 10 | 39.1547 | 144.2993 | 144.2993 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.14 | 130 | 50 | 57 | 7 | 10 | 39.1984 | 145.4141 | 145.4141 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.12 | 180 | 50 | 56 | 6.9 | 10 | 37.7806 | 148.2242 | 148.2242 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.14 | 175 | 50 | 57 | 6.9 | 10 | 37.8646 | 150.5365 | 150.5365 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.16 | 150 | 50 | 58 | 6.9 | 10 | 37.9487 | 152.8378 | 152.8378 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.15 | 160 | 50 | 57.5 | 6.9 | 10 | 37.9066 | 151.6885 | 151.6885 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.11 | 145 | 50 | 55.5 | 6.9 | 9 | 40.2757 | 137.8002 | 137.8002 | yes
11 |  | 125 | 35 | 0 |  |  |  |  | 1.02 | 180 | 50 | 51 | 6.9 | 9 | 39.8726 | 127.9075 | 127.9075 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.24 | 170 | 50 | 62 | 6.9 | 9 | 40.8661 | 151.715 | 151.715 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.27 | 140 | 50 | 63.5 | 7 | 9 | 42.4621 | 149.5452 | 149.5452 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.3 | 175 | 50 | 65 | 7 | 9 | 42.6057 | 152.5618 | 152.5618 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.35 | 180 | 50 | 67.5 | 7 | 9 | 42.8462 | 157.5401 | 157.5401 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.38 | 160 | 50 | 69 | 7 | 9 | 42.9913 | 160.4976 | 160.4976 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.34 | 155 | 50 | 67 | 7 | 9 | 42.798 | 134 | 134 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.35 | 130 | 50 | 67.5 | 7 | 9 | 42.8462 | 157.5401 | 157.5401 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.37 | 200 | 50 | 68.5 | 7 | 9 | 42.9429 | 159.5142 | 159.5142 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.34 | 160 | 50 | 67 | 7 | 9 | 42.798 | 156.5493 | 156.5493 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.33 | 145 | 50 | 66.5 | 7.1 | 9 | 44.2775 | 150.1892 | 150.1892 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.3 | 150 | 50 | 65 | 7.14 | 9 | 44.7531 | 145.2412 | 145.2412 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.31 | 170 | 50 | 65.5 | 7.1 | 9 | 44.1775 | 148.2655 | 148.2655 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.34 | 125 | 50 | 44 | 7.1 | 9 | #REF! | 141 | 141 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.33 | 145 | 50 | 67 | 7.1 | 9 | 44.3276 | 151.1475 | 151.1475 | yes
26 |  | 200 | 35 | 0 |  |  |  |  | 1.12 | 155 | 50 | 56 | 7.1 | 9 | 43.2401 | 129.5094 | 129.5094 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.14 | 145 | 50 | 57 | 7.1 | 9 | 43.3377 | 131.5251 | 131.5251 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.15 | 185 | 50 | 57.5 | 7.1 | 9 | 43.3866 | 132.5293 | 132.5293 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.17 | 145 | 50 | 58.5 | 7.1 | 9 | 43.4846 | 134.5303 | 134.5303 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.14 | 170 | 50 | 57 | 7.1 | 8 | 46.2988 | 123.1134 | 123.1134 | yes
31 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
peter dostert
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel
…..