## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackmas
[7 empty] | clackmas | 2021-12-21
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.24 | 0.22 | 0.22 |  | 0.24
2 |  |  |  | 0.24 | 0.22 | 0.22 | 0.24
3 |  |  | 0.22 | 0.24 | 0.24 |  | 0.24
4 |  |  | 0.24 |  |  | 0.24 | 0.24
5 | 0.24 |  | 0.26 | 0.26 |  |  | 0.26
6 |  |  | 0.24 | 0.24 | 0.26 |  | 0.26
7 |  |  | 0.24 | 0.26 | 0.26 |  | 0.26
8 |  |  | 0.26 | 0.28 | 0.26 |  | 0.28
9 |  |  | 0.302 | 0.28 | 0.28 |  | 0.3
10 |  |  |  | 0.28 | 0.28 |  | 0.28
11 |  |  | 0.26 | 0.28 | 0.28 |  | 0.28
12 |  |  | 0.26 | 0.24 | 0.26 |  | 0.26
13 |  |  |  |  | 0.26 | 0.28 | 0.28
14 |  |  | 0.24 | 0.24 |  |  | 0.24
15 |  |  | 0.24 | 0.26 | 0.26 |  | 0.26
16 |  | 0.24 | 0.24 |  | 0.28 | 0.28 | 0.28
17 | 0.28 | [5 empty] | 0.28
18
19 |  |  | 0.3 | 0.28 |  |  | 0.3
20
21 |  |  |  | 0.28 | 0.28 |  | 0.28
22 |  |  | 0.28 | 0.26 | 0.26 |  | 0.28
23 |  |  | 0.26 | 0.26 |  |  | 0.26
24 |  |  | 0.26 | 0.26 | 0.28 |  | 0.28
25 |  | 0.28 | 0.28 | 0.28 |  |  | 0.28
26 |  |  | 0.26 | 0.26 |  |  | 0.26
27 |  |  | 0.26 | 0.26 | 0.26 |  | 0.26
28 |  |  | 0.26 | 0.26 | 0.24 |  | 0.26
29 |  |  |  | 0.24 | 0.24 | 0.26 | 0.26
30 |  |  | 0.28 | 0.26 |  |  | 0.28
31 |  |  |  | 0.28 | 0.28 | 0.26 | 0.28
0.28 |  |  |  |  | 0.26
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | yes |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Notes: |  |  |  |  | Peter Dostert 6574

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | colton water district |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2021-12-21 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
0.79
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
0.87
1 |  | 125 | 35 | 0 |  |  |  |  | 1.12 | 1401 | 50 | 56 | 7.1 | 8 | 46.1938 | 121.2285 | 121.2285 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.11 | 135 | 50 | 55.5 | 7.1 | 8 | 46.1413 | 120.2826 | 120.2826 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.11 | 120 | 50 | 55.5 | 7.1 | 8 | 46.1413 | 120.2826 | 120.2826 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.1 | 115 | 50 | 55 | 7.1 | 8 | 46.089 | 119.3343 | 119.3343 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.09 | 140 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.08 | 145 | 50 | 54 | 7 | 8 | 44.3917 | 121.6442 | 121.6442 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.09 | 180 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.11 | 135 | 50 | 55.5 | 7 | 8 | 44.5426 | 124.5998 | 124.5998 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.12 | 140 | 50 | 56 | 7 | 8 | 44.593 | 125.5802 | 125.5802 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.13 | 160 | 50 | 56.5 | 7 | 8 | 44.6435 | 126.5582 | 126.5582 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.12 | 180 | 50 | 56 | 7 | 8 | 44.593 | 125.5802 | 125.5802 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.1 | 170 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.14 | 165 | 50 | 57 | 7 | 8 | 44.694 | 127.5338 | 127.5338 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.12 | 145 | 50 | 56 | 6.9 | 8 | 43.0534 | 130.0712 | 130.0712 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.13 | 160 | 50 | 56.5 | 6.9 | 8 | 43.1019 | 131.0847 | 131.0847 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.07 | 130 | 50 | 53.5 | 6.9 | 7 | 45.7327 | 116.9841 | 116.9841 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.03 | 160 | 50 | 51.5 | 6.9 | 7 | 45.5257 | 134 | 134 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.02 | 145 | 50 | 51 | 6.9 | 7 | 45.4742 | 112.1516 | 112.1516 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.01 | 145 | 50 | 50.5 | 6.9 | 7 | 45.4227 | 111.178 | 111.178 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.04 | 160 | 50 | 52 | 6.9 | 7 | 45.5774 | 114.0917 | 114.0917 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.07 | 150 | 50 | 53.5 | 6.9 | 7 | 45.7327 | 116.9841 | 116.9841 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.08 | 160 | 50 | 54 | 6.9 | 7 | 45.7846 | 117.9436 | 117.9436 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.1 | 110 | 50 | 55 | 7 | 7 | 47.5407 | 115.6903 | 115.6903 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.1 | 125 | 50 | 44 | 7 | 7 | #REF! | 141 | 141 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.12 | 160 | 50 | 55 | 6.9 | 7 | 45.8886 | 119.8555 | 119.8555 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.09 | 175 | 50 | 54.5 | 6.9 | 7 | 45.8366 | 118.9007 | 118.9007 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.08 | 165 | 50 | 54 | 6.9 | 7 | 45.7846 | 117.9436 | 117.9436 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.09 | 160 | 50 | 54.5 | 6.9 | 7 | 45.8366 | 118.9007 | 118.9007 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.1 | 170 | 50 | 55 | 6.9 | 7 | 45.8886 | 119.8555 | 119.8555 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.11 | 165 | 50 | 55.5 | 6.9 | 7 | 45.9407 | 120.8079 | 120.8079 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.13 | 130 | 50 | 56.5 | 6.9 | 7 | 46.0451 | 122.7058 | 122.7058 | yes
peter dostert
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel
…..