## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-02-22
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.26 | 0.26 |  |  |  | 0.26
2 |  | 0.24 | 0.24 | 0.24 |  |  | 0.24
3 |  | 0.22 | 0.22 | 0.22 |  |  | 0.22
4 |  |  |  | 0.22 | 0.24 | 0.24 | 0.24
5 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
6 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
7 |  |  | 0.22 |  | 0.22 |  | 0.22
8 |  |  |  | 0.24 | 0.24 |  | 0.24
9 |  |  |  | 0.26 | 0.26 | 0.24 | 0.26
10
11 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
12 |  |  | 0.24 | 0.24 |  |  | 0.24
13 | 0.24 | 0.24 |  |  | 0.24 | 0.24 | 0.24
14 | 0.24 |  |  |  |  | 0.26 | 0.26
15
16 |  |  | 0.26 | 0.24 | 0.22 |  | 0.26
17 |  |  | 0.22 | 0.22 | 0.2 |  | 0.22
18 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
19 |  |  |  | 0.2 | 0.2 | 0.22 | 0.22
20 |  |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
21 |  |  |  | 0.2 | 0.2 | 0.2 | 0.2
22 |  |  |  | 0.2 | 0.22 |  | 0.22
23 |  | 0.22 | 0.2 |  |  |  | 0.22
24 |  | 0.22 | 0.22 | 0.22 |  |  | 0.22
25 |  |  | 0.2 | 0.2 |  |  | 0.2
26 |  | 0.22 | 0.22 |  |  |  | 0.22
27
28 |  |  |  | 0.28 | 0.28 | 0.26 | 0.28
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2022-02-22 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 125 | 35 | 0 |  |  |  |  | 1.06 | 150 | 50 | 53 | 7.1 | 7 | 49.0338 | 108.0886 | 108.0886 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.06 | 160 | 50 | 53 | 7.1 | 7 | 49.0338 | 108.0886 | 108.0886 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.04 | 155 | 50 | 52 | 7.1 | 7 | 48.922 | 106.2917 | 106.2917 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.02 | 165 | 50 | 51 | 7.1 | 7 | 48.8104 | 104.4859 | 104.4859 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.03 | 160 | 50 | 51.5 | 7.1 | 7 | 48.8662 | 105.3899 | 105.3899 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.05 | 185 | 50 | 52.5 | 7.1 | 6 | 52.3661 | 100.2558 | 100.2558 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.06 | 160 | 50 | 53 | 7.1 | 6 | 52.4263 | 101.0944 | 101.0944 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.05 | 150 | 50 | 52.5 | 7.1 | 6 | 52.3661 | 100.2558 | 100.2558 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.08 | 125 | 50 | 54 | 7.1 | 6 | 52.5469 | 102.7654 | 102.7654 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.09 | 130 | 50 | 54.5 | 7.1 | 6 | 52.6073 | 103.5978 | 103.5978 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.1 | 185 | 50 | 55 | 7.1 | 6 | 52.6678 | 104.4281 | 104.4281 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.05 | 140 | 50 | 52.5 | 7.1 | 6 | 52.3661 | 100.2558 | 100.2558 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.07 | 190 | 50 | 53.5 | 7.1 | 6 | 52.4865 | 101.9309 | 101.9309 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.09 | 120 | 50 | 54.5 | 7.1 | 6 | 52.6073 | 103.5978 | 103.5978 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.06 | 135 | 50 | 53 | 7.1 | 6 | 52.4263 | 101.0944 | 101.0944 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.08 | 140 | 50 | 54 | 7.1 | 6 | 52.5469 | 102.7654 | 102.7654 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.1 | 165 | 50 | 55 | 7 | 6 | 50.8201 | 108.225 | 108.225 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.11 | 190 | 50 | 55.5 | 7 | 6 | 50.8783 | 109.0838 | 109.0838 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.11 | 145 | 50 | 55.5 | 7 | 6 | 50.8783 | 109.0838 | 109.0838 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.13 | 155 | 50 | 56.5 | 7 | 6 | 50.9951 | 110.795 | 110.795 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.14 | 175 | 50 | 57 | 7 | 6 | 51.0535 | 111.6475 | 111.6475 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.16 | 150 | 50 | 58 | 7 | 6 | 51.1707 | 113.346 | 113.346 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.15 | 160 | 50 | 57.5 | 7.1 | 6 | 52.9714 | 108.5491 | 108.5491 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.13 | 165 | 50 | 56.5 | 7.1 | 6 | 52.8497 | 106.9069 | 106.9069 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.14 | 180 | 50 | 57 | 7.1 | 6 | 52.9105 | 107.729 | 107.729 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.15 | 145 | 50 | 57.5 | 7.1 | 6 | 52.9714 | 108.5491 | 108.5491 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.16 | 180 | 50 | 58 | 7.1 | 6 | 53.0324 | 109.3671 | 109.3671 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.18 | 160 | 50 | 59 | 7.1 | 6 | 53.1545 | 110.9971 | 110.9971 | yes
29 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
30 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
31 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel