## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | Clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-06-22
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.26 |  |  | 0.24 |  |  | 0.26
2 |  |  | 0.324 | 0.24 |  |  | 0.32
3 | 0.28 | 0.26 |  |  |  | 0.26 | 0.28
4 | 0.3 | 0.28 |  |  |  |  | 0.3
5
6 | 0.24 | 0.24 | 0.24 |  |  |  | 0.24
7 | 0.22 | 0.22 |  |  |  | 0.22 | 0.22
8 | 0.22 | 0.22
9 | 0.24 | 0.24 | 0.24 |  |  |  | 0.24
10 |  |  | 0.28 | 0.28 |  |  | 0.28
11 |  | 0.26 | 0.26 |  |  |  | 0.26
12 |  | 0.24 | 0.26 |  |  |  | 0.26
13 |  | 0.26 | 0.26 |  |  | 0.24 | 0.26
14 | 0.24 | 0.24 |  |  |  |  | 0.24
15 | 0.26 | 0.26 |  |  |  |  | 0.26
16
17 |  |  | 0.28 | 0.3 | 0.28 | 0.28 | 0.3
18 |  |  | 0.24 | 0.24 |  |  | 0.24
19 |  | 0.22 | 0.22 |  |  |  | 0.222
20 |  | 0.22 | 0.24 | 0.24 |  |  | 0.24
21 |  |  | 0.24 | 0.24 |  |  | 0.24
22 |  |  | 0.22 | 0.22 |  |  | 0.24
23 |  |  | 0.26 |  |  |  | 0.26
24
25 |  |  | 0.26 | 0.26 | 0.26 |  | 0.26
26 |  | 0.24 | 0.24 |  |  | 0.24 | 0.24
27 | 0.24 | 0.24 |  |  |  |  | 0.24
28 |  | 0.24 | 0.26 |  |  |  | 0.26
29 |  | 0.26 | 0.26 |  |  | 0.24 | 0.26
30 | 0.24 | 0.24 |  |  |  |  | 0.24
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2022-06-22 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 150 | 35 | 0 |  |  |  |  | 1.1 | 145 | 50 | 55 | 7 | 7 | 47.5407 | 115.6903 | 115.6903 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.08 | 150 | 50 | 54 | 7 | 7 | 47.4326 | 113.8457 | 113.8457 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.07 | 160 | 50 | 53.5 | 7 | 7 | 47.3786 | 112.9201 | 112.9201 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.07 | 190 | 50 | 53.5 | 7 | 7 | 47.3786 | 112.9201 | 112.9201 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.09 | 210 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.06 | 160 | 50 | 53 | 7 | 8 | 44.2915 | 119.6618 | 119.6618 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.1 | 135 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.09 | 140 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.08 | 145 | 50 | 54 | 7 | 8 | 44.3917 | 121.6442 | 121.6442 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.08 | 160 | 50 | 54 | 7.1 | 8 | 45.9845 | 117.4309 | 117.4309 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.07 | 185 | 50 | 53.5 | 7.1 | 8 | 45.9323 | 116.4756 | 116.4756 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.09 | 190 | 50 | 54.5 | 7.1 | 8 | 46.0367 | 118.3838 | 118.3838 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.1 | 155 | 50 | 55 | 7.1 | 8 | 46.089 | 119.3343 | 119.3343 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.11 | 160 | 50 | 55.5 | 7.1 | 8 | 46.1413 | 120.2826 | 120.2826 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.13 | 180 | 50 | 56.5 | 7.1 | 8 | 46.2462 | 122.1721 | 122.1721 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.14 | 170 | 50 | 57 | 7.1 | 8 | 46.2988 | 123.1134 | 123.1134 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.16 | 165 | 50 | 58 | 7.1 | 8 | 46.4041 | 124.9891 | 124.9891 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.18 | 200 | 50 | 59 | 7.1 | 8 | 46.5096 | 126.8555 | 126.8555 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.16 | 220 | 50 | 58 | 7.1 | 8 | 46.4041 | 124.9891 | 124.9891 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.15 | 165 | 50 | 57.5 | 7.1 | 8 | 46.3514 | 124.0524 | 124.0524 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.13 | 175 | 50 | 56.5 | 7.1 | 8 | 46.2462 | 122.1721 | 122.1721 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.06 | 170 | 50 | 53 | 7.1 | 8 | 45.8803 | 115.5181 | 115.5181 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.05 | 155 | 50 | 52.5 | 7.1 | 8 | 45.8282 | 114.5582 | 114.5582 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.06 | 165 | 50 | 53 | 7 | 8 | 44.2915 | 119.6618 | 119.6618 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.6 | 220 | 50 | 80 | 7 | 8 | 47.0884 | 169.8931 | 169.8931 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.3 | 230 | 50 | 65 | 7 | 8 | 45.5113 | 142.8217 | 142.8217 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.05 | 180 | 50 | 52.5 | 7 | 8 | 44.2415 | 118.667 | 118.667 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.04 | 195 | 50 | 52 | 7.0. | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
29 |  |  | 35 | 0 |  |  |  |  | 1.05 | 175 | 50 | 52.5 | 7 | 8 | 44.2415 | 118.667 | 118.667 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.03 | 160 | 50 | 51.5 | 7 | 8 | 44.1416 | 116.6701 | 116.6701 | yes
31 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel