## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-09-22
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.2 |  |  |  | 0.22 | 0.22 | 0.22
2 |  | 0.22 | 0.22 |  |  | 0.22 | 0.22
3 | 0.22 | 0.22 | 0.22 |  |  | 0.22 | 0.222
4 | 0.24 |  |  |  | 0.22 | 0.22 | 0.24
5 | 0.24 |  |  |  |  | 0.24 | 0.24
6 | 0.24 | [5 empty] | 0.24
7
8 |  |  | 0.22 | 0.22 | 0.22 | 0.24 | 0.24
9 | 0.24 |  |  |  | 0.2 |  | 0.24
10 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
11 |  |  | 0.2 | 0.22 |  |  | 0.222
12 |  | 0.22 | 0.2 |  |  |  | 0.22
13 | 0.22 |  |  |  | 0.2 | 0.2 | 0.22
14 | [5 empty] | 0.2 | 0.2
15 | 0.2 | 0.22 |  |  |  | 0.22 | 0.22
16 | 0.22 | 0.22 |  |  |  | 0.22 | 0.22
17 | 0.22 | 0.2 |  |  | 0.24 | 0.24 | 0.24
18 | 0.2 | 0.2 |  |  | 0.22 | 0.22 | 0.22
19 | 0.2 | 0.2 |  |  |  | 0.2 | 0.2
20
21 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
22 |  | 0.2 | 0.2 |  |  |  | 0.2
23 | 0.2 |  |  |  | 0.2 | 0.22 | 0.22
24 |  |  |  | 0.22 | 0.22 | 0.24 | 0.24
25 |  |  |  | 0.22 | 0.22 |  | 0.22
26 |  | 0.22 | 0.24 |  |  |  | 0.24
27 | 0.2 |  |  |  | 0.22 | 0.22 | 0.22
28 |  |  |  | 0.22 | 0.2 |  | 0.22
29 |  |  | 0.2 |  |  | 0.2 | 0.2
30 |  |  | 0.2 | 0.22 |  |  | 0.22
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2022-09-22 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 250 | 35 | 0 |  |  |  |  | 0.92 | 280 | 50 | 46 | 7 | 12 | 33.6298 | 136.7833 | 136.7833 | yes
2 |  |  | 35 | 0 |  |  |  |  | 0.93 | 270 | 50 | 46.5 | 7 | 12 | 33.6666 | 138.1191 | 138.1191 | yes
3 |  |  | 35 | 0 |  |  |  |  | 0.89 | 300 | 50 | 44.5 | 6.9 | 13 | 30.4199 | 146.286 | 146.286 | yes
4 |  |  | 35 | 0 |  |  |  |  | 0.88 | 320 | 50 | 44 | 6.9 | 13 | 30.3872 | 144.798 | 144.798 | yes
5 |  |  | 35 | 0 |  |  |  |  | 0.89 | 265 | 50 | 44.5 | 6.9 | 13 | 30.4199 | 146.286 | 146.286 | yes
6 |  |  | 35 | 0 |  |  |  |  | 0.9 | 285 | 50 | 45 | 6.9 | 13 | 30.4526 | 147.7705 | 147.7705 | yes
7 |  |  | 35 | 0 |  |  |  |  | 0.87 | 290 | 50 | 43.5 | 6.9 | 13 | 30.3545 | 143.3066 | 143.3066 | yes
8 |  |  | 35 | 0 |  |  |  |  | 0.85 | 260 | 50 | 42.5 | 6.9 | 13 | 30.2893 | 140.3136 | 140.3136 | yes
9 |  |  | 35 | 0 |  |  |  |  | 0.86 | 240 | 50 | 43 | 6.9 | 13 | 30.3219 | 141.8118 | 141.8118 | yes
10 |  |  | 35 | 0 |  |  |  |  | 0.84 | 290 | 50 | 42 | 6.9 | 13 | 30.2567 | 138.812 | 138.812 | yes
11 |  |  | 35 | 0 |  |  |  |  | 0.84 | 295 | 50 | 42 | 6.9 | 13 | 30.2567 | 138.812 | 138.812 | yes
12 |  |  | 35 | 0 |  |  |  |  | 0.83 | 250 | 50 | 41.5 | 6.9 | 13 | 30.2242 | 137.307 | 137.307 | yes
13 |  |  | 35 | 0 |  |  |  |  | 0.89 | 230 | 50 | 44.5 | 6.9 | 13 | 30.4199 | 146.286 | 146.286 | yes
14 |  |  | 35 | 0 |  |  |  |  | 0.95 | 225 | 50 | 47.5 | 6.9 | 13 | 30.617 | 155.1427 | 155.1427 | yes
15 |  |  | 35 | 0 |  |  |  |  | 0.92 | 210 | 50 | 46 | 7 | 13 | 31.5607 | 145.751 | 145.751 | yes
16 |  |  | 35 | 0 |  |  |  |  | 0.93 | 185 | 50 | 46.5 | 7 | 13 | 31.5949 | 147.1759 | 147.1759 | yes
17 |  |  | 35 | 0 |  |  |  |  | 0.92 | 170 | 50 | 46 | 7 | 13 | 31.5607 | 145.751 | 145.751 | yes
18 |  |  | 35 | 0 |  |  |  |  | 0.9 | 195 | 50 | 45 | 7 | 13 | 31.4925 | 142.8914 | 142.8914 | yes
19 |  |  | 35 | 0 |  |  |  |  | 0.95 | 260 | 50 | 47.5 | 7 | 13 | 31.6633 | 150.0158 | 150.0158 | yes
20 |  |  | 35 | 0 |  |  |  |  | 0.96 | 200 | 50 | 48 | 7 | 13 | 31.6976 | 151.4309 | 151.4309 | yes
21 |  |  | 35 | 0 |  |  |  |  | 0.92 | 230 | 50 | 46 | 7 | 13 | 31.5607 | 145.751 | 145.751 | yes
22 |  |  | 35 | 0 |  |  |  |  | 0.91 | 240 | 50 | 45.5 | 7 | 13 | 31.5265 | 144.3228 | 144.3228 | yes
23 |  |  | 35 | 0 |  |  |  |  | 0.92 | 220 | 50 | 46 | 7 | 13 | 31.5607 | 145.751 | 145.751 | yes
24 |  |  | 35 | 0 |  |  |  |  | 0.93 | 260 | 50 | 46.5 | 6.9 | 13 | 30.5511 | 152.204 | 152.204 | yes
25 |  |  | 35 | 0 |  |  |  |  | 0.9 | 250 | 50 | 45 | 6.9 | 13 | 30.4526 | 147.7705 | 147.7705 | yes
26 |  |  | 35 | 0 |  |  |  |  | 0.89 | 230 | 50 | 44.5 | 6.9 | 13 | 30.4199 | 146.286 | 146.286 | yes
27 |  |  | 35 | 0 |  |  |  |  | 0.87 | 220 | 50 | 43.5 | 6.9 | 13 | 30.3545 | 143.3066 | 143.3066 | yes
28 |  |  | 35 | 0 |  |  |  |  | 0.92 | 240 | 50 | 46 | 6.9 | 13 | 30.5182 | 150.7295 | 150.7295 | yes
29 |  |  | 35 | 0 |  |  |  |  | 0.94 | 225 | 50 | 47 | 6.9 | 13 | 30.584 | 153.675 | 153.675 | yes
30 |  |  | 35 | 0 |  |  |  |  | 0.95 | 230 | 50 | 47.5 | 6.9 | 13 | 30.617 | 155.1427 | 155.1427 | yes
31 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel