## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-12-22
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.22 | 0.222 |  | 0.22
2 |  |  |  | 0.22 | 0.24 |  | 0.24
3 |  | 0.2 | 0.2 |  |  |  | 0.2
4 |  |  | 0.22 | 0.24 |  |  | 0.24
5 |  |  | 0.22 | 0.22 |  |  | 0.22
6 |  |  |  |  | 0.24 | 0.22 | 0.24
7 |  |  |  |  | 0.22 | 0.22 | 0.22
8 | 0.22 |  | 0.2 | 0.2 |  |  | 0.22
9 |  | 0.22 | 0.2 |  |  |  | 0.22
10 |  |  |  | 0.22 |  |  | 0.22
11 | 0.22 |  | 0.22 |  |  |  | 0.22
12 |  | 0.24 | 0.24 |  |  |  | 0.24
13 |  |  | 0.22 | 0.24 |  |  | 0.24
14
15 |  |  | 0.22 | 0.22 |  |  | 0.22
16 |  |  | 0.24 | 0.24 |  |  | 0.24
17 |  | 0.24 |  |  |  |  | 0.24
18 |  |  | 0.22 | 0.22 |  |  | 0.22
19 |  |  | 0.28 | 0.3 |  |  | 0.3
20 |  | 0.26 | 0.26 |  |  |  | 0.26
21 |  |  | 0.24 | 0.2 | 0.2 |  | 0.24
22
23 |  |  |  | 0.2 | 0.202 | 0.2 | 0.2
24 |  |  | 0.24 | 0.24 |  |  | 0.24
25 |  |  | 0.24 |  |  |  | 0.24
26 | 0.24 | [5 empty] | 0.24
27 | 0.24 | 0.24 | 0.22 |  |  |  | 0.24
28 |  |  |  | 0.22 |  |  | 0.22
29 |  |  |  |  | 0.24 | 0.24 | 0.24
30 |  |  |  | 0.24 | 0.22 |  | 0.24
31 |  |  | 0.24 |  |  | 0.24 | 0.24
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2023-12-22 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 150 | 35 | 0 |  |  |  |  | 1.1 | 150 | 50 | 55 | 6.9 | 9 | 40.2307 | 136.7115 | 136.7115 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.12 | 135 | 50 | 56 | 6.9 | 9 | 40.3208 | 138.8862 | 138.8862 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.13 | 145 | 50 | 56.5 | 7 | 9 | 41.799 | 135.1707 | 135.1707 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.13 | 185 | 50 | 56.5 | 7 | 9 | 41.799 | 135.1707 | 135.1707 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.15 | 160 | 50 | 57.5 | 7 | 9 | 41.893 | 137.2544 | 137.2544 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.13 | 145 | 50 | 56.5 | 7 | 9 | 41.799 | 135.1707 | 135.1707 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.14 | 150 | 50 | 57 | 7 | 9 | 41.846 | 136.2138 | 136.2138 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.12 | 135 | 50 | 56 | 7 | 9 | 41.7521 | 134.1251 | 134.1251 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.13 | 1402 | 50 | 56.5 | 7 | 9 | 41.799 | 135.1707 | 135.1707 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.11 | 180 | 50 | 55.5 | 7 | 9 | 41.7052 | 133.0769 | 133.0769 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.12 | 175 | 50 | 56 | 6.9 | 9 | 40.3208 | 138.8862 | 138.8862 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.13 | 190 | 50 | 56.5 | 6.9 | 9 | 40.3659 | 139.9695 | 139.9695 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.15 | 110 | 50 | 57.5 | 6.9 | 9 | 40.4564 | 142.1285 | 142.1285 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.14 | 140 | 50 | 57 | 6.9 | 9 | 40.4111 | 141.0503 | 141.0503 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.13 | 155 | 50 | 56.5 | 6.9 | 9 | 40.3659 | 139.9695 | 139.9695 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.11 | 160 | 50 | 55.5 | 6.9 | 9 | 40.2757 | 137.8002 | 137.8002 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.1 | 135 | 50 | 55 | 6.9 | 9 | 40.2307 | 136.7115 | 136.7115 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.12 | 170 | 50 | 56 | 6.9 | 8 | 43.0534 | 130.0712 | 130.0712 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.11 | 190 | 50 | 55.5 | 7 | 8 | 44.5426 | 124.5998 | 124.5998 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.09 | 125 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.1 | 135 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.11 | 140 | 50 | 55.5 | 7 | 8 | 44.5426 | 124.5998 | 124.5998 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.09 | 130 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.09 | 180 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.07 | 190 | 50 | 53.5 | 7 | 8 | 44.3416 | 120.6542 | 120.6542 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.1 | 175 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.1 | 140 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.09 | 135 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.08 | 150 | 50 | 54 | 7 | 8 | 44.3917 | 121.6442 | 121.6442 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.09 | 160 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.11 | 190 | 50 | 55.5 | 7 | 8 | 44.5426 | 124.5998 | 124.5998 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel