## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-01-23
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.24 | 0.26 |  |  |  | 0.26
2 |  |  | 0.24 |  |  |  | 0.24
3 |  |  | 0.2 | 0.2 |  |  | 0.2
4 |  |  | 0.22 | 0.22 |  |  | 0.22
5
6 |  |  | 0.24 | 0.24 |  |  | 0.24
7 | 0.24 | 0.26 |  |  |  |  | 0.26
8 | 0.26 | 0.24 |  |  |  | 0.28 | 0.28
9 | 0.24 |  |  |  |  | 0.24 | 0.24
10 | 0.24 |  |  |  | 0.24 | 0.24 | 0.24
11 | 0.24 |  |  |  |  | 0.22 | 0.24
12 | 0.22 | 0.24 |  |  |  | 0.22 | 0.24
13 | 0.24 |  |  |  |  | 0.24 | 0.24
14 | 0.22 |  |  |  |  | 0.26 | 0.26
15 | 0.24 | 0.24 |  |  |  | 0.24 | 0.24
16 | 0.24 |  |  |  |  | 0.24 | 0.24
17 | 0.24 | 0.22 |  |  |  | 0.24 | 0.24
18 | 0.22 |  |  |  |  | 0.26 | 0.26
19 | 0.28 | 0.28 |  |  |  |  | 0.28
20
21
22 |  |  | 0.28 | 0.28 | 0.26 |  | 0.28
23 |  |  | 0.26 |  |  | 0.22 | 0.26
24 | 0.24 |  |  |  | 0.24 | 0.22 | 0.24
25 | 0.22 |  |  |  | 0.24 | 0.26 | 0.26
26 | 0.26 |  |  |  |  | 0.26 | 0.26
27 | 0.26 | 0.26 |  |  |  | 0.26 | 0.26
28 | 0.28 |  |  |  |  | 0.26 | 0.26
29 | 0.24 | 0.22 |  |  |  | 0.22 | 0.24
30 | 0.22 |  |  |  | 0.22 | 0.22 | 0.22
31 | 0.22 |  |  |  |  | 0.22 | 0.22
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2023-01-23 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 150 | 35 | 0 |  |  |  |  | 1.09 | 165 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.11 | 140 | 50 | 55.5 | 6.9 | 8 | 43.0049 | 129.0552 | 129.0552 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.12 | 155 | 50 | 56 | 6.9 | 8 | 43.0534 | 130.0712 | 130.0712 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.13 | 130 | 50 | 56.5 | 6.9 | 8 | 43.1019 | 131.0847 | 131.0847 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.1 | 160 | 50 | 55 | 6.9 | 8 | 42.9564 | 128.0367 | 128.0367 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.09 | 140 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.06 | 180 | 50 | 53 | 6.9 | 8 | 42.7633 | 123.938 | 123.938 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.06 | 195 | 50 | 53 | 6.9 | 8 | 42.7633 | 123.938 | 123.938 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.09 | 130 | 50 | 54.5 | 6.9 | 7 | 45.8366 | 118.9007 | 118.9007 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.13 | 140 | 50 | 56.5 | 6.9 | 7 | 46.0451 | 122.7058 | 122.7058 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.12 | 155 | 50 | 56 | 6.9 | 7 | 45.9928 | 121.7581 | 121.7581 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.16 | 150 | 50 | 58 | 6.9 | 7 | 46.2021 | 125.5353 | 125.5353 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.13 | 130 | 50 | 56.5 | 6.9 | 7 | 46.0451 | 122.7058 | 122.7058 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.09 | 125 | 50 | 54.5 | 6.9 | 7 | #REF! | #REF! | #REF! | #REF!
15 |  |  | 35 | 0 |  |  |  |  | 1.1 | 175 | 50 | 55 | 6.9 | 7 | 45.8886 | 119.8555 | 119.8555 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.11 | 150 | 50 | 55.5 | 6.9 | 7 | 45.9407 | 120.8079 | 120.8079 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.125 | 135 | 50 | 56.25 | 7 | 7 | 47.6763 | 117.9833 | 117.9833 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.1 | 140 | 50 | 55 | 7 | 7 | 47.5407 | 115.6903 | 115.6903 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.15 | 185 | 50 | 57.5 | 7 | 7 | 47.8122 | 120.2622 | 120.2622 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.16 | 190 | 50 | 58 | 7 | 7 | 47.8667 | 121.1698 | 121.1698 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.13 | 175 | 50 | 56.5 | 7 | 7 | 47.7034 | 118.4402 | 118.4402 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.14 | 165 | 50 | 57 | 7 | 7 | 47.7578 | 119.3523 | 119.3523 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.09 | 140 | 50 | 54.5 | 7 | 7 | 47.4866 | 114.7692 | 114.7692 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.08 | 130 | 50 | 54 | 7 | 7 | 47.4326 | 113.8457 | 113.8457 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.06 | 125 | 50 | 53 | 7 | 7 | 47.3247 | 111.9921 | 111.9921 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.02 | 165 | 50 | 51 | 7 | 7 | 47.1099 | 108.2576 | 108.2576 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.06 | 125 | 50 | 53 | 7 | 7 | 47.3247 | 111.9921 | 111.9921 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.03 | 190 | 50 | 51.5 | 7 | 7 | 47.1635 | 109.1947 | 109.1947 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.05 | 200 | 50 | 52.5 | 7 | 7 | 47.2709 | 111.0619 | 111.0619 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.08 | 150 | 50 | 54 | 7 | 7 | 47.4326 | 113.8457 | 113.8457 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.18 | 160 | 50 | 59 | 7 | 7 | 47.9759 | 122.9784 | 122.9784 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel
Not sure what happend on line 21