## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-05-23
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.28 | 0.26 | 0.26 |  | 0.28
2 |  |  | 0.26 | 0.26 | 0.26 |  | 0.26
3 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
4 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
5
6 |  |  | 0.24 | 0.24 | 0.24 |  | 0.24
7 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
8 |  | 0.22 |  |  |  | 0.24 | 0.24
9 | 0.24 |  |  |  | 0.22 | 0.24 | 0.24
10 |  | 0.22 | 0.22 |  |  | 0.22 | 0.22
11 |  |  | 0.22 | 0.22 |  |  | 0.22
12 |  |  | 0.24 | 0.22 |  |  | 0.24
13 |  |  |  |  | 0.22 | 0.24 | 0.24
14 | 0.24 | [5 empty] | 0.24
15
16 |  |  | 0.28 | 0.28 | 0.28 | 0.26 | 0.28
17 |  |  | 0.28 | 0.3 | 0.3 |  | 0.3
18
19 |  |  | 0.22 | 0.22 | 0.24 | 0.24 | 0.24
20 |  |  | 0.2 | 0.22 |  |  | 0.22
21 |  | 0.24 | 0.24 | 0.24 |  |  | 0.24
22 |  |  | 0.24 | 0.26 |  |  | 0.26
23 | 0.26 | 0.28 |  |  |  | 0.28 | 0.28
24 |  |  | 0.28 | 0.28 |  | 0.26 | 0.28
25 |  |  | 0.26 | 0.28 | 0.28 |  | 0.28
26 |  |  | 0.28 | 0.28 |  |  | 0.28
27 |  |  | 0.26 | 0.26 |  | 0.28 | 0.28
28 |  |  | 0.28 |  |  |  | 0.28
29 | 0.26 |  | 0.26 | 0.26 |  |  | 0.26
30 |  |  | 0.28 | 0.26 | 0.26 |  | 0.28
31 |  |  | 0.26 | 0.28 |  |  | 0.28
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2023-05-23 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 125 | 35 | 0 |  |  |  |  | 1.08 | 150 | 50 | 54 | 7 | 8 | 44.3917 | 121.6442 | 121.6442 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.1 | 155 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.11 | 160 | 50 | 55.5 | 7 | 8 | 44.5426 | 124.5998 | 124.5998 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.13 | 140 | 50 | 56.5 | 7 | 8 | 44.6435 | 126.5582 | 126.5582 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.12 | 165 | 50 | 56 | 7 | 8 | 44.593 | 125.5802 | 125.5802 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.14 | 145 | 50 | 57 | 7 | 8 | 44.694 | 127.5338 | 127.5338 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.11 | 200 | 50 | 55.5 | 7 | 8 | 44.5426 | 124.5998 | 124.5998 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.1 | 170 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.09 | 110 | 50 | 54.5 | 7 | 8 | 44.442 | 122.6318 | 122.6318 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.1 | 185 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.12 | 160 | 50 | 56 | 7 | 8 | 44.593 | 125.5802 | 125.5802 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.11 | 175 | 50 | 55.5 | 7 | 8 | 44.5426 | 124.5998 | 124.5998 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.1 | 125 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.1 | 190 | 50 | 55 | 7 | 8 | 44.4923 | 123.617 | 123.617 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.09 | 210 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.08 | 180 | 50 | 54 | 6.9 | 8 | 42.8598 | 125.9923 | 125.9923 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.09 | 165 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.07 | 190 | 50 | 53.5 | 6.9 | 8 | 42.8115 | 124.9664 | 124.9664 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.09 | 185 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
20 |  | 200 | 35 | 0 |  |  |  |  | 1.1 | 210 | 50 | 55 | 6.9 | 8 | 42.9564 | 128.0367 | 128.0367 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.01 | 220 | 50 | 50.5 | 6.9 | 8 | 42.5233 | 118.7584 | 118.7584 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.02 | 235 | 50 | 51 | 6.9 | 8 | 42.5712 | 119.7994 | 119.7994 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.03 | 250 | 50 | 51.5 | 6.9 | 8 | 42.6191 | 120.8378 | 120.8378 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.02 | 210 | 50 | 51 | 6.9 | 8 | 42.5712 | 119.7994 | 119.7994 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.03 | 195 | 50 | 51.5 | 6.9 | 8 | 42.6191 | 120.8378 | 120.8378 | yes
26 |  |  | 35 | 0 |  |  |  |  | 0.99 | 180 | 50 | 49.5 | 7 | 9 | 41.1474 | 120.2992 | 120.2992 | yes
27 |  |  | 35 | 0 |  |  |  |  | 0.98 | 220 | 50 | 49 | 7 | 9 | 41.1013 | 119.2177 | 119.2177 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.1 | 230 | 50 | 55 | 7 | 9 | 41.6584 | 132.0262 | 132.0262 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.09 | 200 | 50 | 54.5 | 7 | 9 | 41.6117 | 130.9729 | 130.9729 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.11 | 190 | 50 | 55.5 | 7 | 9 | 41.7052 | 133.0769 | 133.0769 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.12 | 200 | 50 | 56 | 7 | 9 | 41.7521 | 134.1251 | 134.1251 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel