## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-07-23
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.26 | 0.24 | 0.24 |  | 0.26
2 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
3 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
4 |  |  | 0.22 | 0.24 | 0.22 | 0.22 | 0.24
5 |  |  | 0.2 | 0.22 |  | 0.22 | 0.22
6 | 0.24 |  |  | 0.22 |  |  | 0.24
7 |  |  |  | 0.22 | 0.22 |  | 0.22
8 |  | 0.22 | 0.24 | 0.22 |  | 0.22 | 0.24
9 |  |  | 0.22 | 0.2 | 0.2 | 0.2 | 0.22
10 | 0.22 |  |  | 0.24 | 0.22 |  | 0.24
11 |  |  |  | 0.22 | 0.2 | 0.2 | 0.22
12 |  |  |  | 0.22 | 0.2 | 0.2 | 0.22
13 | 0.2 | [5 empty] | 0.2
14
15 |  |  | 0.22 | 0.22 | 0.22 | 0.24 | 0.24
16 | 0.22 | 0.22 | 0.22 | 0.22 | 0.24 |  | 0.24
17 |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
18 |  |  | 0.24 | 0.22 | 0.22 |  | 0.24
19 |  | 0.22 | 0.24 | 0.24 | 0.24 |  | 0.24
20 |  |  | 0.2 | 0.22 | 0.22 | 0.22 | 0.222
21 |  |  | 0.24 | 0.22 | 0.24 | 0.24 | 0.24
22 |  |  | 0.26 | 0.22 | 0.22 | 0.22 | 0.26
23 |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
24 | 0.22 |  | 0.28 | 0.24 | 0.24 |  | 0.28
25 |  |  | 0.26 | 0.24 |  | 0.24 | 0.26
26 | 0.24 |  |  | 0.24 | 0.22 | 0.22 | 0.24
27 |  |  | 0.26 | 0.24 | 0.22 |  | 0.26
28 |  |  | 0.24 | 0.22 | 0.22 |  | 0.24
29 |  |  | 0.24 | 0.22 | 0.22 | 0.24 | 0.24
30 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
31 |  |  | 0.22 | 0.24 | 0.24 |  | 0.24
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
0 | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2023-07-23 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 250 | 35 | 0 |  |  |  |  | 1.05 | 190 | 50 | 52.5 | 6.9 | 11 | 35.1476 | 149.3701 | 149.3701 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.03 | 250 | 50 | 51.5 | 6.9 | 11 | 35.0704 | 146.8474 | 146.8474 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.06 | 260 | 50 | 53 | 6.9 | 11 | 35.1863 | 150.627 | 150.627 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.02 | 260 | 50 | 51 | 7 | 11 | 36.2534 | 140.6765 | 140.6765 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.01 | 195 | 50 | 50.5 | 7 | 11 | 36.2134 | 139.4512 | 139.4512 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1 | 190 | 50 | 50 | 7 | 11 | 36.1734 | 138.2229 | 138.2229 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.02 | 190 | 50 | 51 | 7 | 11 | 36.2534 | 140.6765 | 140.6765 | yes
8 |  |  | 35 | 0 |  |  |  |  | 0.99 | 210 | 50 | 49.5 | 7 | 11 | 36.1335 | 136.9918 | 136.9918 | yes
9 |  |  | 35 | 0 |  |  |  |  | 0.99 | 280 | 50 | 49.5 | 7 | 12 | 33.8881 | 146.0688 | 146.0688 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.02 | 240 | 50 | 51 | 7 | 12 | 33.9995 | 150.0021 | 150.0021 | yes
11 |  |  | 35 | 0 |  |  |  |  | 0.98 | 235 | 50 | 49 | 7 | 12 | 33.8511 | 144.7516 | 144.7516 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.01 | 220 | 50 | 50.5 | 7 | 12 | 33.9624 | 148.694 | 148.694 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.02 | 255 | 50 | 51 | 7 | 12 | 33.9995 | 150.0021 | 150.0021 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.05 | 275 | 50 | 52.5 | 6.9 | 12 | 32.9716 | 159.228 | 159.228 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.09 | 290 | 50 | 54.5 | 6.9 | 12 | 33.1156 | 164.5749 | 164.5749 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.08 | 210 | 50 | 54 | 6.9 | 12 | 33.0795 | 163.2429 | 163.2429 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.09 | 230 | 50 | 54.5 | 6.9 | 12 | 33.1156 | 164.5749 | 164.5749 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.1 | 220 | 50 | 55 | 6.9 | 12 | 33.1517 | 165.9038 | 165.9038 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.15 | 240 | 50 | 57.5 | 6.9 | 12 | 33.333 | 172.5017 | 172.5017 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.12 | 190 | 50 | 56 | 6.9 | 12 | 33.2241 | 168.5523 | 168.5523 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.13 | 225 | 50 | 56.5 | 6.9 | 12 | 33.2604 | 169.8718 | 169.8718 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.12 | 265 | 50 | 56 | 6.9 | 12 | 33.2241 | 168.5523 | 168.5523 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.14 | 300 | 50 | 57 | 6.9 | 12 | 33.2967 | 171.1883 | 171.1883 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.11 | 220 | 50 | 55.5 | 6.9 | 12 | 33.1879 | 167.2296 | 167.2296 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.09 | 260 | 50 | 54.5 | 7 | 12 | 34.2611 | 159.0726 | 159.0726 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.09 | 240 | 50 | 54.5 | 7 | 12 | 34.2611 | 159.0726 | 159.0726 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.11 | 235 | 50 | 55.5 | 7 | 12 | 34.3362 | 161.6368 | 161.6368 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.12 | 240 | 50 | 56 | 7 | 12 | 34.3739 | 162.9144 | 162.9144 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.13 | 295 | 50 | 56.5 | 7 | 12 | 34.4116 | 164.1889 | 164.1889 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.12 | 320 | 50 | 56 | 7 | 12 | 34.3739 | 162.9144 | 162.9144 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.09 | 245 | 50 | 54.5 | 7 | 12 | 34.2611 | 159.0726 | 159.0726 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel