## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-08-23
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.24 | 0.24 | 0.24 | 0.22 |  | 0.24
2 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
3 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
4 |  |  | 0.22 | 0.24 | 0.22 |  | 0.24
5 |  | 0.26 | 0.24 | 0.22 | 0.22 | 0.22 | 0.26
6 | 0.22 |  | 0.22 | 0.22 | 0.2 |  | 0.22
7 |  | 0.22 | 0.22 | 0.22 |  | 0.24 | 0.24
8 | 0.24 |  |  | 0.22 | 0.22 | 0.22 | 0.24
9 |  |  | 0.22 | 0.22 |  | 0.22 | 0.22
10 |  |  | 0.22 | 0.2 |  | 0.2 | 0.22
11 |  |  | 0.2 | 0.2 |  |  | 0.2
12 | 0.22 | 0.22 | 0.22 |  | 0.22 | 0.2 | 0.22
13 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
14
15 |  |  | 0.24 | 0.22 | 0.2 | 0.2 | 0.24
16 | 0.2 |  |  | 0.22 | 0.22 | 0.22 | 0.22
17 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
18 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
19 |  |  | 0.22 | 0.22 |  | 0.22 | 0.22
20 | 0.24 |  | 0.24 | 0.22 | 0.22 | 0.22 | 0.24
21 |  |  | 0.22 | 0.24 | 0.24 |  | 0.24
22 |  |  | 0.24 | 0.24 | 0.24 | 0.22 | 0.24
23 |  |  | 0.24 | 0.22 | 0.22 |  | 0.24
24 |  | 0.26 | 0.22 | 0.22 | 0.22 |  | 0.26
25 |  | 0.24 | 0.24 | 0.24 |  | 0.2 | 0.24
26 |  |  | 0.22 | 0.22 |  | 0.22 | 0.22
27 |  |  | 0.22 |  | 0.22 | 0.24 | 0.24
28 |  | 0.26 | 0.28 |  |  | 0.28 | 0.28
29 |  |  | 0.26 | 0.26 |  |  | 0.26
30 | 0.26 |  |  | 0.26 | 0.24 |  | 0.26
31 |  |  | 0.24 | 0.24 |  |  | 0.24
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2023-08-23 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 250 | 35 | 0 |  |  |  |  | 1.06 | 260 | 50 | 53 | 7 | 12 | 34.1487 | 155.2035 | 155.2035 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.03 | 220 | 50 | 51.5 | 7 | 13 | 31.939 | 161.2451 | 161.2451 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.01 | 230 | 50 | 50.5 | 7 | 13 | 31.8698 | 158.4573 | 158.4573 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1 | 260 | 50 | 50 | 7 | 13 | 31.8353 | 157.0585 | 157.0585 | yes
5 |  |  | 35 | 0 |  |  |  |  | 0.99 | 290 | 50 | 49.5 | 7 | 13 | 31.8008 | 155.6565 | 155.6565 | yes
6 |  |  | 35 | 0 |  |  |  |  | 0.95 | 310 | 50 | 47.5 | 7 | 13 | 31.6633 | 150.0158 | 150.0158 | yes
7 |  |  | 35 | 0 |  |  |  |  | 0.92 | 240 | 50 | 46 | 7 | 13 | 31.5607 | 145.751 | 145.751 | yes
8 |  |  | 35 | 0 |  |  |  |  | 0.96 | 230 | 50 | 48 | 6.9 | 13 | 30.65 | 156.607 | 156.607 | yes
9 |  |  | 35 | 0 |  |  |  |  | 0.98 | 210 | 50 | 49 | 6.9 | 13 | 30.7161 | 159.5256 | 159.5256 | yes
10 |  |  | 35 | 0 |  |  |  |  | 0.96 | 250 | 50 | 48 | 6.9 | 13 | 30.65 | 156.607 | 156.607 | yes
11 |  |  | 35 | 0 |  |  |  |  | 0.97 | 235 | 50 | 48.5 | 6.9 | 13 | 30.683 | 158.068 | 158.068 | yes
12 |  |  | 35 | 0 |  |  |  |  | 0.97 | 290 | 50 | 48.5 | 6.9 | 13 | 30.683 | 158.068 | 158.068 | yes
13 |  |  | 35 | 0 |  |  |  |  | 0.96 | 320 | 50 | 48 | 6.9 | 13 | 30.65 | 156.607 | 156.607 | yes
14 |  |  | 35 | 0 |  |  |  |  | 0.96 | 260 | 50 | 48 | 6.9 | 13 | 30.65 | 156.607 | 156.607 | yes
15 |  |  | 35 | 0 |  |  |  |  | 0.94 | 250 | 50 | 47 | 6.9 | 13 | 30.584 | 153.675 | 153.675 | yes
16 |  |  | 35 | 0 |  |  |  |  | 0.94 | 255 | 50 | 47 | 6.9 | 13 | 30.584 | 153.675 | 153.675 | yes
17 |  |  | 35 | 0 |  |  |  |  | 0.96 | 240 | 50 | 48 | 6.9 | 13 | 30.65 | 156.607 | 156.607 | yes
18 |  |  | 35 | 0 |  |  |  |  | 0.95 | 210 | 50 | 47.5 | 7 | 13 | 31.6633 | 150.0158 | 150.0158 | yes
19 |  |  | 35 | 0 |  |  |  |  | 0.93 | 280 | 50 | 46.5 | 7 | 13 | 31.5949 | 147.1759 | 147.1759 | yes
20 |  |  | 35 | 0 |  |  |  |  | 0.94 | 335 | 50 | 47 | 7 | 13 | 31.6291 | 148.5975 | 148.5975 | yes
21 |  |  | 35 | 0 |  |  |  |  | 0.99 | 270 | 50 | 49.5 | 7 | 13 | 31.8008 | 155.6565 | 155.6565 | yes
22 |  |  | 35 | 0 |  |  |  |  | 0.96 | 250 | 50 | 48 | 7 | 13 | 31.6976 | 151.4309 | 151.4309 | yes
23 |  |  | 35 | 0 |  |  |  |  | 0.98 | 260 | 50 | 49 | 7 | 13 | 31.7664 | 154.2512 | 154.2512 | yes
24 |  |  | 35 | 0 |  |  |  |  | 0.95 | 245 | 50 | 47.5 | 7 | 13 | 31.6633 | 150.0158 | 150.0158 | yes
25 |  |  | 35 | 0 |  |  |  |  | 0.95 | 260 | 50 | 47.5 | 7 | 13 | 31.6633 | 150.0158 | 150.0158 | yes
26 |  |  | 35 | 0 |  |  |  |  | 0.99 | 280 | 50 | 49.5 | 7 | 13 | 31.8008 | 155.6565 | 155.6565 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1 | 295 | 50 | 50 | 6.9 | 13 | 30.7824 | 162.4307 | 162.4307 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.01 | 220 | 50 | 50.5 | 6.9 | 13 | 30.8156 | 163.8783 | 163.8783 | yes
29 |  |  | 35 | 0 |  |  |  |  | 0.99 | 200 | 50 | 49.5 | 6.9 | 13 | 30.7492 | 160.9798 | 160.9798 | yes
30 |  |  | 35 | 0 |  |  |  |  | 0.98 | 210 | 50 | 49 | 6.9 | 13 | 30.7161 | 159.5256 | 159.5256 | yes
31 |  |  | 35 | 0 |  |  |  |  | 0.97 | 250 | 50 | 48.5 | 6.9 | 12 | 32.6857 | 148.383 | 148.383 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel