## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-11-23
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.26 | 0.26 |  |  | 0.26
2 |  |  | 0.26 | 0.28 |  |  | 0.28
3 |  |  | 0.28 | 0.28 |  |  | 0.28
4 |  |  | 0.3 | 0.28 |  |  | 0.3
5 |  |  | 0.28 | 0.3 |  |  | 0.3
6
7 |  |  |  | 0.3 | 0.3 | 0.28 | 0.3
8 |  |  | 0.28 | 0.26 | 0.24 |  | 0.28
9 |  |  | 0.24 | 0.24 |  |  | 0.24
10 | 0.26 | 0.26 |  |  | 0.24 |  | 0.26
11 |  | 0.26 | 0.26 |  |  | 0.28 | 0.28
12 |  |  | 0.28 | 0.26 |  |  | 0.28
13 |  |  | 0.26 | 0.24 |  |  | 0.26
14 | 0.24 |  |  | 0.24 | 0.24 |  | 0.24
15 |  |  | 0.26 | 0.24 | 0.24 |  | 0.26
16
17 |  |  |  | 0.24 | 0.24 |  | 0.24
18 |  |  | 0.26 | 0.26 |  |  | 0.26
19 |  |  |  | 0.28 | 0.28 |  | 0.28
20 |  |  |  | 0.24 | 0.24 | 0.24 | 0.24
21 |  |  | 0.24 | 0.24 |  |  | 0.24
22 |  |  | 0.26 | 0.24 |  |  | 0.26
23 | 0.24 | 0.24 |  |  |  | 0.24 | 0.24
24 |  |  | 0.26 | 0.26 |  |  | 0.26
25 |  |  | 0.24 |  |  | 0.24 | 0.24
26 |  |  | 0.24 | 0.26 |  |  | 0.26
27 | 0.26 |  |  |  | 0.24 | 0.26 | 0.26
28
29 |  |  | 0.26 | 0.24 | 0.24 |  | 0.26
30 |  |  |  | 0.26 | 0.24 | 0.24 | 0.26
31 |  |  | 0.26 | 0.26 | 0.28 |  | 0.28
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2023-11-23 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 150 | 35 | 0 |  |  |  |  | 1.02 | 170 | 50 | 51 | 6.9 | 10 | 37.3639 | 136.4953 | 136.4953 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.02 | 140 | 50 | 51 | 6.9 | 9 | 39.8726 | 127.9075 | 127.9075 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.04 | 125 | 50 | 52 | 6.69 | 9 | 37.1595 | 139.9372 | 139.9372 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1 | 180 | 50 | 50 | 6.9 | 9 | 39.7836 | 125.68 | 125.68 | yes
5 |  |  | 35 | 0 |  |  |  |  | 0.99 | 190 | 50 | 49.5 | 6.8 | 9 | 38.3847 | 128.9576 | 128.9576 | yes
6 |  |  | 35 | 0 |  |  |  |  | 0.98 | 140 | 50 | 49 | 6.8 | 9 | 38.3421 | 127.797 | 127.797 | yes
7 |  |  | 35 | 0 |  |  |  |  | 0.99 | 165 | 50 | 49.5 | 6.8 | 9 | 38.3847 | 128.9576 | 128.9576 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.014 | 160 | 50 | 50.7 | 6.9 | 9 | 39.8458 | 127.2404 | 127.2404 | yes
9 |  |  | 35 | 0 |  |  |  |  | 0.98 | 175 | 50 | 49 | 6.9 | 9 | 39.6948 | 123.4417 | 123.4417 | yes
10 |  |  | 35 | 0 |  |  |  |  | 0.97 | 160 | 50 | 48.5 | 6.9 | 9 | 39.6505 | 122.3186 | 122.3186 | yes
11 |  |  | 35 | 0 |  |  |  |  | 0.96 | 200 | 50 | 48 | 6.9 | 9 | 39.6063 | 121.1928 | 121.1928 | yes
12 |  |  | 35 | 0 |  |  |  |  | 0.96 | 190 | 50 | 48 | 6.9 | 9 | 39.6063 | 121.1928 | 121.1928 | yes
13 |  |  | 35 | 0 |  |  |  |  | 0.95 | 195 | 50 | 47.5 | 6.9 | 9 | 39.5621 | 120.0643 | 120.0643 | yes
14 |  |  | 35 | 0 |  |  |  |  | 0.97 | 150 | 50 | 48.5 | 6.9 | 9 | 39.6505 | 122.3186 | 122.3186 | yes
15 |  |  | 35 | 0 |  |  |  |  | 0.94 | 125 | 50 | 47 | 6.9 | 9 | 39.518 | 118.9332 | 118.9332 | yes
16 |  |  | 35 | 0 |  |  |  |  | 0.98 | 50 | 50 | 49 | 6.9 | 9 | 39.6948 | 123.4417 | 123.4417 | yes
17 |  |  | 35 | 0 |  |  |  |  | 0.98 | 195 | 50 | 49 | 6.8 | 9 | 38.3421 | 127.797 | 127.797 | yes
18 |  |  | 35 | 0 |  |  |  |  | 0.98 | 210 | 50 | 49 | 6.8 | 9 | 38.3421 | 127.797 | 127.797 | yes
19 |  |  | 35 | 0 |  |  |  |  | 0.96 | 160 | 50 | 48 | 6.8 | 9 | 38.2569 | 125.4676 | 125.4676 | yes
20 |  |  | 35 | 0 |  |  |  |  | 0.92 | 135 | 50 | 46 | 6.9 | 9 | 39.4299 | 116.6627 | 116.6627 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1 | 140 | 50 | 50 | 6.9 | 9 | 39.7836 | 125.68 | 125.68 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.02 | 190 | 50 | 51 | 6.9 | 9 | 39.8726 | 127.9075 | 127.9075 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.03 | 185 | 50 | 51.5 | 6.9 | 9 | 39.9171 | 129.0173 | 129.0173 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.04 | 190 | 50 | 52 | 6.9 | 9 | #REF! | #REF! | #REF! | #REF!
25 |  |  | 35 | 0 |  |  |  |  | 1.03 | 160 | 50 | 51.5 | 6.9 | 9 | 39.9171 | 129.0173 | 129.0173 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.03 | 135 | 50 | 51.5 | 6.9 | 9 | 39.9171 | 129.0173 | 129.0173 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.02 | 160 | 50 | 51 | 6.9 | 8 | 42.5712 | 119.7994 | 119.7994 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.05 | 70 | 50 | 52.5 | 6.9 | 8 | 42.7152 | 122.9071 | 122.9071 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.04 | 210 | 50 | 52 | 6.9 | 8 | 42.6671 | 121.8737 | 121.8737 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.04 | 200 | 50 | 52 | 6.9 | 8 | 42.6671 | 121.8737 | 121.8737 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.02 | 180 | 50 | 51 | 6.9 | 8 | 42.5712 | 119.7994 | 119.7994 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel